## Instructions
Press UP or DOWN ARROW in column A to read through the document. Note: This worksheet is just text and has no input areas. The text is broken into multiple cells for ease of reading.
Readily Available Permit: Simple Cycle Turbine
Air Permits Division
Texas Commission on Environmental Quality
TCEQ 20858, Version 3.3
This sheet is for informational purposes only. No data is required and you do not need to print this sheet. This sheet provides guidance on the RAP-SCT criteria and instructions for preparing and submitting an application.
I. Overview
The RAP-SCT is a New Source Review (NSR) initial permit to authorize operations of an electric utility simple cycle turbine facility. This application workbook provides administrative and technical information needed by the Texas Commission on Environmental Quality (TCEQ) to evaluate the new sources. The qualification criteria for this RAP is contained within this workbook and must be agreed to prior to submittal of a RAP application. Facilities shall be constructed and operated as specified in the permit application for the permit. All representations regarding construction plans and operation requirements contained in the permit application (including this workbook) shall be enforceable representations upon issuance of the permit. Under Texas Government Code 559.003(a), individuals are entitled to receive and review any information collected by TCEQ about the individual by means of a form that that is completed and filed with TCEQ in a paper or electronic format on the TCEQ website consistent with Texas Government Code sec., 559.003(b). The individual is also entitled to have TCEQ correct information about the individual that is incorrect. If you have questions on how to fill out this form or about the Air Permits Division, please contact us at 512-239-1250.
This cell left intentionally blank.
II. Qualification Criteria
The following qualification criteria must be met in order to submit an application for the RAP-SCT. 1. The project is for an electric utility simple cycle turbine facility at a greenfield site. 2. The project is a minor source. 3. The sources included in the RAP-SCT are limited to: two simple cycle turbines, one fire water pump, two dew point heaters, two lube oil vents, six tanks storing diesel or lube oil, one emergency generator engine, fugitive emissions, and maintenance, startup and shutdown (MSS) activities. 4. The setback distance from the property line to the closest emission point is 150 meters, except for El Paso County (300 meters) and Harris County (420 meters). 5. The customer has a compliance history classification of Satisfactory or High (further information on compliance history classifications and details on obtaining a compliance history report can be found at the links listed at the end of this sheet). 6. The facility will comply with all of the following, as listed in this workbook: • Emission sources and rates; • Best Available Control Technology (BACT); • The Air Quality Analysis; • Special Conditions; and • Representations made in this application workbook.
This cell left intentionally blank.
III. Process Instructions
1. Prepare all items to make the complete application. Follow "Section IV. Workbook Instructions" below to complete the application workbook. A complete application for this RAP includes the following: • Process Flow Diagram • Current Area Map • Plot Plan • RAP-SCT Workbook (The file name should be: Date_ApplicationWorkbook_Company name_Permit number) 2. Submit the application through STEERS as an ePermits application. When submitting through STEERS a wet signature is not required and the system will notify the appropriate regional office and local program(s). You are still required to provide a hard copy of the application to be displayed at the public viewing location during public notice. 3. Submit all application attachments through STEERS as part of your ePermit application unless: • the file size of an attachment exceeds 50 MB or • the file type is not accepted (accepted file types are xls, xlsm, xlsx, txt, pdf, doc, docx, wpd, csv, xml, jpg, gif, tif, and jpeg). If the attachment cannot be submitted through STEERS for one of the reasons listed above, submit the attachment through email or TCEQ FTPS. For the initial submittal, you must share these files with APIRT@tceq.texas.gov. Once your project is assigned, you will share files directly with your reviewer. If confidential files will be submitted, follow the additional instructions below. Confidential files must be submitted through STEERS or the TCEQ FTPS. All pages must be marked confidential and have confidential in the file name. Confidential submittals must be separate from non-confidential application materials. Note: emails sent to the agency are not encryption protected via Secure Sockets Layers by our server and may be subject to interception by common third-party internet tools. Anything marked as confidential will be treated as such by APD staff upon receipt.
4. Submit copies of the application materials to other applicable program areas in accordance with "Section VI. Where to Submit Application Materials" below. 5. Do not begin construction until notified by the TCEQ. 6. If the qualification criteria are not met, or if the applicant does not agree with the RAP-SCT Special Conditions, the applicant will receive notice that the application has been voided and the applicant should seek a different type of authorization as appropriate. See the below link for additional information about submitting via FTPS:
https://ftps.tceq.texas.gov/help/
This cell left intentionally blank.
IV. Workbook Instructions
1. Complete the workbook sheets in order, moving left to right and top to bottom. 2. Complete all blank cells on each applicable emission source sheet. • Each emission point is identified with a pre-assigned emission point identification number (EPN) which cannot be changed. The emission point is defined as the point from which air contaminants enter the ambient air. • Some cells have drop-down selections. 3. On the "Emission Summary" sheet, confirm acceptance of all information in this workbook and submitted with the application. 4. If a cell displays “Error,” the project does not qualify for the RAP-SCT, or an error has been made on the entry. Revise the data entered for that source. 5. Air Quality Analyses (AQAs) were performed in support of the RAP-SCT. AQAs were performed for each of the sixteen TCEQ regions. Each of the AQA reports summarizes the results for the respective TCEQ region and includes information specific to the counties of that respective region. Each of the AQA reports can be located under the RAP-SCT Resources heading at:
https://www.tceq.texas.gov/permitting/air/guidance/newsourcereview/rap/rap-sct.html
This cell left intentionally blank.
V. Website Links:
Combustion BACT | https://www.tceq.texas.gov/permitting/air/nav/air_bact_combustsources.html
Core Data Form | https://www.tceq.texas.gov/permitting/central_registry/guidance.html
TCEQ Regional Offices | http://www.tceq.texas.gov/agency/directory/region
Local Air Pollution Control Offices | http://www.tceq.texas.gov/permitting/air/local_programs.html
Compliance history classifications | http://www.tceq.texas.gov/compliance/enforcement/compliance-history/about.html
Compliance history report | http://www.tceq.texas.gov/compliance/enforcement/compliance-history/get_report.html
This cell left intentionally blank.
VI. Where to Submit Application Materials
Who | Where | When | What
Air Permits Division Air Permits Initial Review Team (APIRT) | STEERS | All applications | Completed RAP-SCT application workbook
Air Permits Division Air Permits Initial Review Team (APIRT) | STEERS unless file size or type are not compatible, in which case submit through email or TCEQ FTPS (APIRT@tceq.texas.gov) | All applications | Application attachments
Alabama-Coushatta Tribe of Texas | 571 State Park Road 56, Livingston, Texas 77351 | If the proposed facilities are located within 100 km or less of the Indian Tribal Lands | Copies of the RAP-SCT application workbook, all attachments, public notice, and affidavit
Mr. Hector Canales, Kickapoo Traditional Tribe of Texas Public Works | 2212 Rosita Valley Road Eagle Pass, TX 78852 | If the proposed facilities are located within 100 km or less of the Indian Tribal Lands | Copies of the RAP-SCT application workbook, all attachments, public notice, and affidavit
Ysleta del Sur Pueblo of Texas | 119 S. Old Pueblo Rd., El Paso, Texas 79907 | If the proposed facilities are located within 100 km or less of the Indian Tribal Lands | Copies of the RAP-SCT application workbook, all attachments, public notice, and affidavit
Environmental Management Division Chief International Boundary and Water Commission United States Section | 4171 N. Mesa, Suite C-100, El Paso, Texas 79902-1441 | If new construction is proposed within 100 km of the Rio Grande River | Copies of the RAP-SCT application workbook and all attachments
This cell left intentionally blank.
VII. Workbook Table of Contents (click to jump to the worksheet)
Instructions
General application materials
PI-1-SCT: General Application for Simple Cycle Turbine RAP
Estimated Capital Cost and Fee Verification
Specific source information (sheets not needed for this project will be greyed out)
Simple Cycle Turbine–1
Simple Cycle Turbine–2
Fire Water Pump
Dew Point Heater–1
Dew Point Heater–2
Lube Oil Vent–1
Lube Oil Vent–2
Tank–1
Tank–2
Tank–3
Tank–4
Tank–5
Tank–6
Emergency Engine
Fugitive Emissions
Maintenance Activities
Additional application materials
Best Available Control Technology (BACT)
Special Conditions
Public Notice Applicability, Required Information, and Small Business Classification
Emission Summary
End of worksheet

## PI-1-SCT
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Form PI-1-SCT: General Information for RAP-SCT
This sheet provides general information needed by the TCEQ and is required for this RAP. Instructions: 1. Complete all applicable sections below.
This cell intentionally left blank
I. Applicant Information
I acknowledge that I am submitting an authorized TCEQ application workbook and any necessary attachments. Except for inputting the requested data and adjusting row height, I have not changed the TCEQ application workbook in any way, including but not limited to changing formulas, formatting, content, or protections.
A. Company Information
Company or Legal Name:
Permits are issued to either the facility owner or operator, commonly referred to as the applicant or permit holder. List the legal name of the company, corporation, partnership, or person who is applying for the permit. We will verify the legal name with the Texas Secretary of State at (512) 463-5555 or at:
www.sos.state.tx.us
Texas Secretary of State Charter/Registration Number (if given):
B. Company Official Contact Information: Must not be a consultant.
Prefix (Mr., Ms., Dr., etc.):
First Name:
Last Name:
Title:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
C. Technical Contact Information: This person must have the authority to make binding agreements and representations on behalf of the applicant and may be a consultant.
Prefix (Mr., Ms., Dr., etc.):
First Name:
Last Name:
Title:
Company or Legal Name:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
D. Assigned Numbers
The CN and RN below are assigned when a Core Data Form is initially submitted to the Central Registry. The RN is also assigned if the agency has conducted an investigation or if the agency has issued an enforcement action. If these numbers have not yet been assigned, leave these questions blank.
Enter the CN. The CN is a unique number given to each business, governmental body, association, individual, or other entity that owns, operates, is responsible for, or is affiliated with a regulated entity.
Enter the RN. The RN is a unique agency assigned number given to each person, organization, place, or thing that is of environmental interest to us and where regulated activities will occur. The RN replaces existing air account numbers. The RN for portable units is assigned to the unit itself, and that same RN should be used when applying for authorization at a different location.
This cell intentionally left blank
II. Delinquent Fees and Penalties
Does the applicant have unpaid delinquent fees and/or penalties owed to the TCEQ? This form will not be processed until all delinquent fees and/or penalties owed to the TCEQ or the Office of the Attorney General on behalf of the TCEQ is paid in accordance with the Delinquent Fee and Penalty Protocol. For more information regarding Delinquent Fees and Penalties, go to the TCEQ Web site at:
www.tceq.texas.gov/agency/financial/fees/delin
This cell intentionally left blank
III. Facility Location and General Information
A. Location
Is this an existing site?
County: Enter the county where the facility is physically located.
Street Address:
City: If the address is not located in a city, then enter the city or town closest to the facility, even if it is not in the same county as the facility.
ZIP Code: Please include the ZIP Code of the physical facility site, not the ZIP Code of the applicant's mailing address.
Site Location Description: If there is no street address, provide written driving directions to the site. Identify the location by distance and direction from well-known landmarks such as major highway intersections.
Use USGS maps, county maps prepared by the Texas Department of Transportation, or an online software application such as Google Earth to find the latitude and longitude.
Latitude (in degrees, minutes, and nearest second (DDD:MM:SS)) for the street address or the destination point of the driving directions. Latitude is the angular distance of a location north of the equator and will always be between 25 and 37 degrees north (N) in Texas.
Longitude (in degrees, minutes, and nearest second (DDD:MM:SS)) for the street address or the destination point of the driving directions. Longitude is the angular distance of a location west of the prime meridian and will always be between 93 and 107 degrees west (W) in Texas.
B. General Information
Site Name:
Area Name: Must indicate the general type of operation, process, equipment or facility. Include numerical designations, if appropriate. Examples are Sulfuric Acid Plant and No. 5 Steam Boiler. Vague names such as Chemical Plant are not acceptable.
Distance from the property line to the closest emission point (in meters): Minimums: 300 for El Paso County, 420 for Harris County, 150 for all other counties
Are there any schools located within 3,000 feet of the site boundary?
C. Industry Type
Principal Company Product/Business:
A list of SIC codes can be found at:
https://www.naics.com/sic-codes-industry-drilldown/
Principal SIC code:
NAICS codes and conversions between NAICS and SIC Codes are available at:
https://www.census.gov/naics/
Principal NAICS code:
D. State Senator and Representative for this site
This information can be found at (note, this site is not compatible with Internet Explorer):
fyi.capitol.texas.gov/Home.aspx
State Senator:
District:
State Representative:
District:
This cell intentionally left blank
IV. Project Information
A. Description
Revise the provided process description to represent your project and site specifics. (Limited to 5000 characters.) | This application is to construct a new simple cycle electric generating facility to provide peaking electric power to the grid. The facility will have a maximum total power generation capacity of approximately xx MW and will operate xx simple cycle turbines with associated equipment.
B. Equipment to be Authorized by this Permit
How many simple cycle turbines will this permit include?
Will this permit include a fire water pump?
How many dew point heaters will this permit include?
How many lube oil vents will this permit include?
How many tanks for storing diesel or lube oil will this permit include?
Will this permit include an emergency generator engine?
Will this permit include fugitive emissions?
Will this permit include maintenance, startup, and shutdown activities?
C. Project Timing You must obtain an air authorization before beginning construction. Construction is broadly interpreted as anything other than site clearance or site preparation. Enter the date as "Month Date, Year" (e.g. July 4, 1776).
Projected Start of Construction:
Projected Start of Operation:
D. Enforcement Projects
Is this application in response to, or related to, an agency investigation, notice of violation, or enforcement action?
If yes, did you attach copies of any correspondence from the agency and provide the RN associated with the investigation, notice of violation, or enforcement action?
E. Mass Emissions Cap and Trade
Is this facility located at a site within the Houston/Galveston nonattainment area (Brazoria, Chambers, Fort Bend, Galveston, Harris, Liberty, Montgomery, and Waller Counties)?
Is Mass Emissions Cap and Trade applicable to the new facilities?
If MECT is applicable, does the application contain documentation demonstrating that the proposed facility, group of facilities, or account has obtained allowances to operate?
This cell intentionally left blank
V. Federal Regulatory Questions
The following requirements apply to the proposed facility.
A. Title 40 CFR Part 60
Which NSPS subpart(s) apply to the facility in this application? | Subparts A and KKKK (if including turbines) and IIII (if including engines)
B. Title 40 CFR Part 61
Which NSPS subpart(s) apply to the facility in this application? | None
C. Title 40 CFR Part 63
Which NSPS subpart(s) apply to the facility in this application? | Subparts A and ZZZZ (if including engines)
This cell intentionally left blank
VI. Required Attachments
A. Confidential Application Materials
Is confidential information submitted with this application?
If yes, is each confidential page marked "CONFIDENTIAL" in large red letters?
THSC §382.041 restricts whether confidential information can be disclosed. Mark any information related to secret or proprietary processes or methods of manufacture as confidential if you do not want this information in the public file. All confidential information should be separated from the application and submitted as a separate file. Additional information regarding confidential information can be found at the link below:
www.tceq.texas.gov/permitting/air/confidential.html
B. Is the Core Data Form (Form 10400) attached? Only necessary if facilities are located within 100 km or less of Indian Tribal Lands or the Rio Grande River.
C. Is a current area map attached?
Is the area map a current map with a true north arrow, an accurate scale, the entire plant property, the location of the property relative to prominent geographical features including, but not limited to, highways, roads, streams, and significant landmarks such as buildings, residences, schools, parks, hospitals, day care centers, and churches?
Does the map show a 3,000-foot radius from the property boundary?
D. Is a plot plan attached?
Does your plot plan clearly show a north arrow, an accurate scale, all property lines, all emission points, buildings, tanks, process vessels, other process equipment, and two bench mark locations?
Does your plot plan identify all emission points on the affected property?
E. Is a process flow diagram attached?
Is the process flow diagram sufficiently descriptive so the permit reviewer can determine the raw materials to be used in the process; all major processing steps and major equipment items; individual emission points associated with each process step; the location and identification of all emission abatement devices; and the location and identification of all waste streams (including wastewater streams that may have associated air emissions)?
F. Is a Public Involvement Plan (PIP) required for this project?
Is the PIP Form (TCEQ Form 20960) attached?
Requirements can be found at the following link: |  | https://www.tceq.texas.gov/permitting/air#pip
This cell intentionally left blank
VII. Signature
Will the proposed facilities be located within 100 km of Indian Tribal Lands and/or the Rio Grande River? If yes, sign the section below prior to mailing copies of this application (more details on the Instructions sheet). All applications will be signed during the STEERS submittal process.
The owner or operator of the facility must apply for authority to construct. The appropriate company official (owner, plant manager, president, vice president, or environmental director) must sign all copies of the application. The applicant’s consultant cannot sign the application. Important Note: Signatures must be original in ink, not reproduced by photocopy, fax, or other means, and must be received before any permit is issued.
The signature below confirms that I have knowledge of the facts included in this application and that these facts are true and correct to the best of my knowledge and belief. I further state that to the best of my knowledge and belief, the project for which application is made will not in any way violate any provision of the Texas Water Code (TWC), Chapter 7; the Texas Health and Safety Code, Chapter 382; the Texas Clean Air Act (TCAA); the air quality rules of the Texas Commission on Environmental Quality; or any local governmental ordinance or resolution enacted pursuant to the TCAA. I further state that I understand my signature indicates that this application meets all applicable nonattainment, prevention of significant deterioration, or major source of hazardous air pollutant permitting requirements. The signature further signifies awareness that intentionally or knowingly making or causing to be made false material statements or representations in the application is a criminal offense subject to criminal penalties.
Name:
Signature:
Original signature is required.
Date:
End of worksheet

## Fees
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Estimated Capital Cost and Fee Verification
This sheet determines application fee requirements for this application. Payment is part of the STEERS submittal process and fees are due and payable at the time an application is filed. Required fees must be received before the agency will consider an application to be complete. Applications will not be considered for review nor will any time constraints required of TCEQ for application processing begin until a fee is received. (30 TAC § 116.143) All permit fees shall be remitted by credit card or ACH (electronic funds transfer). Instructions for online payment through the ePay system can be found at:
www3.tceq.texas.gov/epay/
Instructions: 1. Answer each of the questions in Section I. 2. Enter the amount of each cost in the associated box. Include estimated cost of equipment and services that would normally be capitalized according to standard and generally accepted corporate financing and accounting procedures. 3. Enter payment information. 4. If applicable, submit the application under the seal of a Texas Licensed P.E.
I. General Information
Is this project for new facilities controlled and operated directly by the federal government? (30 TAC § 116.141(b)(1) and 30 TAC § 116.163(a))
A fee of $75,000 shall be required if no estimate of capital project cost is included with the permit application. (30 TAC § 116.141(d)) Select "yes" here to use this option. Then skip sections II and III.
Select Application Type
This cell intentionally left blank
II. Direct Costs
Type of Cost |  |  | Amount
Process and control equipment not previously owned by the applicant and not currently authorized under this chapter.
Auxiliary equipment, including exhaust hoods, ducting, fans, pumps, piping, conveyors, stacks, storage tanks, waste disposal facilities, and air pollution control equipment specifically needed to meet permit and regulation requirements.
Freight charges.
Site preparation, including demolition, construction of fences, outdoor lighting, road, and parking areas.
Installation, including foundations, erection of supporting structures, enclosures or weather protection, insulation and painting, utilities and connections, process integration, and process control equipment.
Auxiliary buildings, including materials storage, employee facilities, and changes to existing structures.
Ambient air monitoring network.
Sub-Total: |  |  | 0
This cell intentionally left blank
III. Indirect Costs
Type of Cost |  |  | Amount
Final engineering design and supervision, and administrative overhead.
Construction expense, including construction liaison, securing local building permits, insurance, temporary construction facilities, and construction clean-up.
Contractor's fee and overhead.
Sub-Total: |  |  | 0
This cell intentionally left blank
IV. Calculations
In signing the application in STEERS with this fee sheet attached, I certify that the total estimated capital cost of the project as defined in 30 TAC §116.141 is equal to or less than the above figure. I further state that I have read and understand Texas Water Code § 7.179, which defines Criminal Offenses for certain violations, including intentionally or knowingly making, or causing to be made, false material statements or representations.
Estimated Capital Cost | Minor Application Fee
Less than $300,000 | $900 (minimum fee)
$300,000 - $25,000,000 | 0.30% of capital cost
Greater than $25,000,000 | $75,000 (maximum fee)
This cell intentionally left blank
Your estimated capital cost: |  | 0
Permit Application Fee: |  | FALSE
If a fee exemption or reduction applies, describe how this facility qualifies for an exemption or reduction. Include the actual fee amount.
This cell intentionally left blank
V. Payment Information
Enter the fee amount to be paid:
This cell intentionally left blank
VI. Professional Engineer Seal Requirement
Is the estimated capital cost of the project above $2 million?
Is this project subject to an exemption contained in the Texas Engineering Practice Act (TEPA)? (30 TAC § 116.110(f))
Is the application required to be submitted under the seal of a Texas licensed P.E.? Note: an electronic PE seal is acceptable.
End of worksheet

## Simple Cycle Turbine–1
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Simple Cycle Turbine–1
This sheet details turbine specifications and determines emission rates. Instructions: 1. Complete all information below. 2. Each turbine is limited to operating no more than 2500 hours per year.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | CTG1 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 80 ft
Diameter (ft) |  | 15 ft
Temperature (°F) |  | 756 oF
Velocity (fps) |  | 52.4 fps
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum (if applicable) and Unit
Fuel type | natural gas | NA
Number of operating hours per year |  | 2500 hours
Rated baseload capacity at site conditions (MW) |  | MW
Heat rate of turbine, HHV basis (Btu/kW-hr) |  | Btu/kW-hr
Higher heating value of natural gas fuel (Btu/scf) |  | Btu/scf
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
NOX | 0 | 0
CO | 0 | 0
PM | 0 | 0
PM10 | 0 | 0
PM2.5 | 0 | 0
VOC | 0 | 0
SO2 | 0 | 0
H2SO4 | 0 | 0
This cell left intentionally blank.
V. Calculation Methodology
A. NOx, CO, and VOC emissions
Calculations use the published F-factors for natural gas (40 CFR Pt. 60, Appendix A-7, Method 19, Table 19-2.). In this case, the appropriate F­ factor is F=8710 dscf exhaust (stoichiometric air) per MMBtu fuel fired.
Short-term NOx emissions: The exhaust volume is estimated by applying the F-factor to the total heat duty. NOx emissions are then calculated by correcting the exhaust volume to 15% O2, and applying the NOx BACT concentration limit of 9 ppmvd (15% O2). The molecular weight of NO2 is used. Emission rate = rated baseload capacity x heat rate x (1 kW x MMBtu/1000 MW x Btu) x (8710 dscf/MMBtu) x (1 lb-mol/379 dscf) x 0.000009 x ((20.9% - 0%)/(20.9% - 15%)) x (46 lb NO2/lb-mol)
Short-term CO emissions: The same approach is used as for calculating NOx emissions, except that the molecular weight of CO (28 lb/lb-mol) is applied. Note that the same numerical BACT limit of 9 ppmvd at 15% O2 applies.
Short-term VOC emissions: The same approach is used as for calculating NOx emissions, except that the molecular weight is assumed to be that of propane (44 lb/lb-mol) and the BACT limit is 2 ppmvd propane equivalent at 15% O2.
Long-term emissions: This is determined based on the limited hours of operation of the turbine per year entered above. Emission rate = short term lb/hr x hr per yr/2000 lb/t
B. PM and SOx (SO2 and SO3) emissions
Particulate and SOx emission rates are determined from the total amount of fuel combusted, applying the appropriate emission factor.
Short-term SO2 emissions: The hourly fuel usage is determined by dividing the total heat duty by the higher heating value of the natural gas fuel. SO2 emissions are then calculated by applying the BACT fuel sulfur content limit and assuming 100% conversion of fuel-bound sulfur to SO2. Emission rate = 1000 kW x (rated baseload capacity x heat rate/heating value) x (2 gr sulfur/100 scf) x (1 lb/7000 gr) x (64 lb SO2/32 lb S)
Short-term H2SO4 emissions: Assume that 5% of total sulfur in the fuel gas is converted to SO3 and that 100% of SO3 combines with water to form H2SO4 mist. The SO2 emission rate equation can then be used, adjusting for the molecular weight of H2SO4.
Short-term PM emissions: Assume that all particulate is PM2.5 (i.e., PM=PM10=PM2.5), and use the AP-42 emission factor for natural gas combustion, 0.0075 lb/MMBtu (HHV).
Long-term SOx emissions: SOx emissions are calculated by multiplying the short-term emission rate by hrs/yr/2000 lb/t and adjusting downward for the annual BACT limit of 0.25 gr S/100 scf. Emission rate = short term lb/hr x (hrs/yr/2000 lb/t) x (0.25/2)
Long term PM emissions: Particulate emissions are calculated in the same manner, except that no adjustment of the emission factor is required.
End of worksheet

## Simple Cycle Turbine–2
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Simple Cycle Turbine–2
This sheet details turbine specifications and determines emission rates. Instructions: 1. Complete all information below. 2. Each turbine is limited to operating no more than 2500 hours per year.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | CTG2 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 80 ft
Diameter (ft) |  | 15 ft
Temperature (°F) |  | 756 oF
Velocity (fps) |  | 52.4 fps
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum (if applicable) and Unit
Fuel type | natural gas | NA
Number of operating hours per year |  | 2500 hours
Rated baseload capacity at site conditions (MW) |  | MW
Heat rate of turbine, HHV basis (Btu/kW-hr) |  | Btu/kW-hr
Higher heating value of natural gas fuel (Btu/scf) |  | Btu/scf
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
NOX | 0 | 0
CO | 0 | 0
PM | 0 | 0
PM10 | 0 | 0
PM2.5 | 0 | 0
VOC | 0 | 0
SO2 | 0 | 0
H2SO4 | 0 | 0
This cell left intentionally blank.
V. Calculation Methodology
A. NOx, CO, and VOC emissions
Calculations use the published F-factors for natural gas (40 CFR Pt. 60, Appendix A-7, Method 19, Table 19-2.). In this case, the appropriate F­ factor is F=8710 dscf exhaust (stoichiometric air) per MMBtu fuel fired.
Short-term NOx emissions: The exhaust volume is estimated by applying the F-factor to the total heat duty. NOx emissions are then calculated by correcting the exhaust volume to 15% O2, and applying the NOx BACT concentration limit of 9 ppmvd (15% O2). The molecular weight of NO2 is used. Emission rate = rated baseload capacity x heat rate x (1 kW x MMBtu/1000 MW x Btu) x (8710 dscf/MMBtu) x (1 lb-mol/379 dscf) x 0.000009 x ((20.9% - 0%)/(20.9% - 15%)) x (46 lb NO2/lb-mol)
Short-term CO emissions: The same approach is used as for calculating NOx emissions, except that the molecular weight of CO (28 lb/lb-mol) is applied. Note that the same numerical BACT limit of 9 ppmvd at 15% O2 applies.
Short-term VOC emissions: The same approach is used as for calculating NOx emissions, except that the molecular weight is assumed to be that of propane (44 lb/lb-mol) and the BACT limit is 2 ppmvd propane equivalent at 15% O2.
Long-term emissions: This is determined based on the limited hours of operation of the turbine per year entered above. Emission rate = short term lb/hr x hr per yr/2000 lb/t
B. PM and SOx (SO2 and SO3) emissions
Particulate and SOx emission rates are determined from the total amount of fuel combusted, applying the appropriate emission factor.
Short-term SO2 emissions: The hourly fuel usage is determined by dividing the total heat duty by the higher heating value of the natural gas fuel. SO2 emissions are then calculated by applying the BACT fuel sulfur content limit and assuming 100% conversion of fuel-bound sulfur to SO2. Emission rate = 1000 kW x (rated baseload capacity x heat rate/heating value) x (2 gr sulfur/100 scf) x (1 lb/7000 gr) x (64 lb SO2/32 lb S)
Short-term H2SO4 emissions: Assume that 5% of total sulfur in the fuel gas is converted to SO3 and that 100% of SO3 combines with water to form H2SO4 mist. The SO2 emission rate equation can then be used, adjusting for the molecular weight of H2SO4.
Short-term PM emissions: Assume that all particulate is PM2.5 (i.e., PM=PM10=PM2.5), and use the AP-42 emission factor for natural gas combustion, 0.0075 lb/MMBtu (HHV).
Long-term SOx emissions: SOx emissions are calculated by multiplying the short-term emission rate by hrs/yr/2000 lb/t and adjusting downward for the annual BACT limit of 0.25 gr S/100 scf. Emission rate = short term lb/hr x (hrs/yr/2000 lb/t) x (0.25/2)
Long term PM emissions: Particulate emissions are calculated in the same manner, except that no adjustment of the emission factor is required.
End of worksheet

## Fire Water Pump
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Fire Water Pump
This sheet details fire water pump specifications and determines emission rates. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | FWP | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 7 ft
Diameter (ft) |  | 0.33 ft
Temperature (°F) |  | 821 oF
Velocity (fps) |  | 90 fps
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Rated brake power of engine (hp) |  | 184.22 hp
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | Emission Factor | Emission Factor Unit | lb/hr | tpy
NOX | 4.56 | g/hp-hr | 0 | 0
CO | 2.62 | g/hp-hr | 0 | 0
PM | 0.16 | g/hp-hr | 0 | 0
PM10 | 0.16 | g/hp-hr | 0 | 0
PM2.5 | 0.16 | g/hp-hr | 0 | 0
VOC | 0.24 | g/hp-hr | 0 | 0
SO2 | 0.0049 | g/hp-hr | 0 | 0
This cell left intentionally blank.
V. Calculation Methodology
A. Short-term emissions (NOx, CO, PM, VOC) Emission rates are calculated based on EPA performance standards for non-road engines (40 CFR § 89.112), which are consistent with current BACT. The short-term emission rate is obtained by multiplying the engine's rated brake power by the appropriate emission factor, and then converting from grams to pounds. All particulate is assumed to be emitted as PM2.5. Emission rate = engine brake power x emission factor x (1 lb/453.6 g)
B. Short-term emissions (SO2) Emission rates are estimated based on the fuel consumption rate and the use of ultra-low sulfur diesel (ULSD), which contains at most 15 ppmw total sulfur. The fuel consumption rate depends on the design of the engine. A reasonable approximation for fuel consumption can be made by assuming an energy content of 137,000 Btu/gal for diesel fuel, a density of 7.1 lb/gal, and a brake-specific fuel consumption (BSFC) of 7,000 Btu/hp-hr (AP-42 Section 3.3. This equates to a thermal efficiency of approximately 36%.) Fuel consumption (gal/hr) = engine brake power x (1 gal/137,000 Btu) x (7.1 lb/gal) Emission rate = fuel consumption x engine brake power x (15 lb S/1,000,000 lb diesel) x (64 lb SO2/32 lb S)
C. Annual emissions Current BACT tracks MACT ZZZZ in limiting the engines to 100 hr/yr of non-emergency use. Therefore, annual emission rates for all pollutants can be determined by multiplying the short-term emission rate by 100 hr/yr and by 1 ton/2000 lb.
End of worksheet

## Dew Point Heater–1
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Dew Point Heater–1
This sheet details dew point heater specifications and determines emission rates. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | HEAT1 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 20 ft
Diameter (ft) |  | 0.67 ft
Temperature (°F) |  | 700 oF
Velocity (fps) |  | 40 fps
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Heater design firing rate (MMBtu/hr) |  | 5.99 MMBtu/hr
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr Emission Factor lb/hr per MMBtu/hr | tpy Emission Factor | lb/hr | tpy
NOX | 0.06 | 0.06 | 0 | 0
CO | 0.082 | 0.082 | 0 | 0
PM | 0.0075 | 0.0075 | 0 | 0
PM10 | 0.0075 | 0.0075 | 0 | 0
PM2.5 | 0.0075 | 0.0075 | 0 | 0
VOC | 0.005 | 0.005 | 0 | 0
SO2 | 0.0056 | 0.0014 | 0 | 0
This cell left intentionally blank.
V. Calculation Methodology
The NOx emission factor is based on the current BACT level. The SO2 emission factor is based on the permit fuel sulfur limits. Other pollutant emission factors are based on AP-42 emission factors. Annual emission rates are conservatively based on 2000 hr/yr of operation.
End of worksheet

## Dew Point Heater–2
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Dew Point Heater–2
This sheet details dew point heater specifications and determines emission rates. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | HEAT2 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 20 ft
Diameter (ft) |  | 0.67 ft
Temperature (°F) |  | 700 oF
Velocity (fps) |  | 40 fps
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Heater design firing rate (MMBtu/hr) |  | 5.99 MMBtu/hr
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr Emission Factor lb/hr per MMBtu/hr | tpy Emission Factor | lb/hr | tpy
NOX | 0.06 | 0.06 | 0 | 0
CO | 0.082 | 0.082 | 0 | 0
PM | 0.0075 | 0.0075 | 0 | 0
PM10 | 0.0075 | 0.0075 | 0 | 0
PM2.5 | 0.0075 | 0.0075 | 0 | 0
VOC | 0.005 | 0.005 | 0 | 0
SO2 | 0.0056 | 0.0014 | 0 | 0
This cell left intentionally blank.
V. Calculation Methodology
The NOx emission factor is based on the current BACT level. The SO2 emission factor is based on the permit fuel sulfur limits. Other pollutant emission factors are based on AP-42 emission factors. Annual emission rates are conservatively based on 2000 hr/yr of operation.
End of worksheet

## Lube Oil Vent–1
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Lube Oil Vent-1
This sheet details lube oil vent specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | LOV1 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 20 ft
This cell left intentionally blank.
III. Project Emission Rates
Pollutant | lb/hr | tpy
PM | 0.05 | 0.1
PM10 | 0.05 | 0.1
PM2.5 | 0.05 | 0.1
VOC | 0.05 | 0.1
This cell left intentionally blank.
IV. Calculation Methodology
Gas turbines make use of oil which is used to lubricate and cool the compressor and turbine bearings. Lube oil is continuously circulated throughout the gas turbine assembly, and a supply of lube oil is maintained in a reservoir inside of the assembly. Leaks of lube oil (which would foul the turbine blades) are prevented through the use of "seal air," which is bled from the compressor and supplied to the exterior of bearing boxes, creating a lower pressure in the interior of the bearing boxes than in their supporting part. High-pressure seal air then becomes dissolved in the circulating lube oil, and eventual deaeration in the lube oil reservoir gives rise to a fine mist of lube oil from the vent of the lube oil reservoir. In order to prevent safety hazards in the operating area (slip hazards from an oil slick on the ground), waste of lube oil, and air emissions, modern gas turbine assemblies include an oil mist eliminator at the lube oil reservoir vent. The oil mist droplets passing through the mist eliminators are very fine (diameter < 2.5 µm). While emissions from lube oil vents primarily take the form of lube oil aerosol, a small fraction of oil vapors is also present.
Current BACT requires the use of a high efficiency oil mist eliminators of a type which are designed to remove 99% or greater of particulate emissions, and operation of the turbine so as to result in no visible emissions. Emission rates from turbine lube oil vents are typically estimated based on total lubricating oil usage rates for similar installations, with calculated emission rates ranging from 0.01-0.1 lb/hr. These emission calculations use a mass balance approach, with estimates of lube oil consumption ranging from 0.01-0.3 gal/day, and assume that all lube oil used by the turbine is eventually emitted as particulate and/or VOC through the lube oil vent.
Since satisfactory emission factors are not available for estimating controlled emission rates of lube oil mist, a mass balance approach is a reasonable means of estimating emis­sions. Default emission rates of 0.05 lb/hr and 0.1 tpy should be used for each turbine. These apply for PM, PM10 , PM2.5, and VOC. The default emission rate is expected to be representative provided that high efficiency oil mist eliminators are used, the eliminators are kept in good working order at all times, and no visible emissions are released from the lube oil vents.
End of worksheet

## Lube Oil Vent–2
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Lube Oil Vent-2
This sheet details lube oil vent specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | LOV2 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 20 ft
This cell left intentionally blank.
III. Project Emission Rates
Pollutant | lb/hr | tpy
PM | 0.05 | 0.1
PM10 | 0.05 | 0.1
PM2.5 | 0.05 | 0.1
VOC | 0.05 | 0.1
This cell left intentionally blank.
IV. Calculation Methodology
Gas turbines make use of oil which is used to lubricate and cool the compressor and turbine bearings. Lube oil is continuously circulated throughout the gas turbine assembly, and a supply of lube oil is maintained in a reservoir inside of the assembly. Leaks of lube oil (which would foul the turbine blades) are prevented through the use of "seal air," which is bled from the compressor and supplied to the exterior of bearing boxes, creating a lower pressure in the interior of the bearing boxes than in their supporting part. High-pressure seal air then becomes dissolved in the circulating lube oil, and eventual deaeration in the lube oil reservoir gives rise to a fine mist of lube oil from the vent of the lube oil reservoir. In order to prevent safety hazards in the operating area (slip hazards from an oil slick on the ground), waste of lube oil, and air emissions, modern gas turbine assemblies include an oil mist eliminator at the lube oil reservoir vent. The oil mist droplets passing through the mist eliminators are very fine (diameter < 2.5 µm). While emissions from lube oil vents primarily take the form of lube oil aerosol, a small fraction of oil vapors is also present.
Current BACT requires the use of a high efficiency oil mist eliminators of a type which are designed to remove 99% or greater of particulate emissions, and operation of the turbine so as to result in no visible emissions. Emission rates from turbine lube oil vents are typically estimated based on total lubricating oil usage rates for similar installations, with calculated emission rates ranging from 0.01-0.1 lb/hr. These emission calculations use a mass balance approach, with estimates of lube oil consumption ranging from 0.01-0.3 gal/day, and assume that all lube oil used by the turbine is eventually emitted as particulate and/or VOC through the lube oil vent.
Since satisfactory emission factors are not available for estimating controlled emission rates of lube oil mist, a mass balance approach is a reasonable means of estimating emis­sions. Default emission rates of 0.05 lb/hr and 0.1 tpy should be used for each turbine. These apply for PM, PM10 , PM2.5, and VOC. The default emission rate is expected to be representative provided that high efficiency oil mist eliminators are used, the eliminators are kept in good working order at all times, and no visible emissions are released from the lube oil vents.
End of worksheet

## Tank–1
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Tank-1
This sheet details tank specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | TANK1 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Material stored |  | diesel or lube oil
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.01 | 0.02
This cell left intentionally blank.
V. Calculation Methodology
A. Overview Diesel and lube oil storage tanks maintained at a gas turbine installation, which are to be used exclusively in supplying diesel and lube oil to the turbine and emergency engines, have low overall capacities and throughputs. Considering that both diesel fuel and lube oil have low volatility, default emission rates are recommended for these sources. The default emission rates are expected to be representative so long as current BACT is applied (requiring that the tank be bottom- or submerged-fill and be painted white), and use of the tanks is only to support operation of the simple cycle turbines and associated equipment.
Default VOC emission rates of 0.01 lb/hr and 0.02 tpy should be used for both lube oil and diesel fuel tanks. An explanation of how these rates were derived follows. While a typical size for a diesel storage tank is 500 gal, the permit should not place a numerical limit on the size of the storage tanks, so long as tanks are installed only for use in operating and maintaining the turbines and associated emergency diesel engines.
B. Short Term Emissions A typical short-term emission rate can be calculated using the equation provided in TCEQ publication APDG 6250, "Estimating Short Term Emission Rates from Tanks", September 2014). Lmax = (average vapor molecular weight x vapor pressure / ideal gas constant of 80.273 x temperature Rankine) x maximum filling rate Average vapor molecular weight and vapor pressure are estimated using data in AP-42 Chapter 7, Table 7.1-2 for No. 2 Distillate Fuel Oil. The vapor pressure of 0.02 psia corresponds to 1 mmHg, and is a reasonable estimate of the vapor pressure of both diesel fuel and turbine oil. A worst case temperature and maximum filling rate of 95°F and 200 gal/hr (respectively) are assumed, giving the following: Lmax = [(130 lb/lb-mol x 0.02 psia) / ((80.273 psia x gal/lb-mol x ⁰R) x 555 ⁰R)] x 200 gal/hr = 0.012 lb/hr
C. Long-Term Emission Rates Standing and working losses are estimated following AP-42, Chapter 7, equations 1-2 and 1-29.
To estimate standing losses, the vapor space volume is conservatively assumed to equal 500 gal (the volume of the tank), and a stock vapor density of 0.00046 lb/ft3 is estimated based on an average temperature of 70°F and the vapor pressure and molecular weight values noted above. A vapor space expansion factor of 0.05 is determined by assuming that the tank paint is white and in good condition, and conservative figures of 30°R and 1800 Btu/ft2 are assumed for the daily temperature range and annual average solar insolation. The vented vapor saturation factor is assumed to be 1 (based on the maximum value of that variable). Total standing losses for this scenario are: Ls = (365 yr)(66.8 ft3)(0.00046 lb/ft3)(0.05)(1) = 0.6 lb/yr
To estimate working losses, the vapor pressure and molecular weight values noted above are used, and a total throughput of 5,000 gal is assumed. KN and KP values of 1 each are selected for fewer than 36 turnovers/yr and non-crude oil product. Lw = (0.001 lb-mol/psia x Bbl)(130 lb/lb-mol)(0.02 psia)(119 Bbl/yr)(1)(1) = 0.3 lb/yr
The total annual emissions is determined by adding the standing and working losses and is less than 0.01 tpy.
End of worksheet

## Tank–2
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Tank-2
This sheet details tank specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | TANK2 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Material stored |  | diesel or lube oil
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.01 | 0.02
This cell left intentionally blank.
V. Calculation Methodology
A. Overview Diesel and lube oil storage tanks maintained at a gas turbine installation, which are to be used exclusively in supplying diesel and lube oil to the turbine and emergency engines, have low overall capacities and throughputs. Considering that both diesel fuel and lube oil have low volatility, default emission rates are recommended for these sources. The default emission rates are expected to be representative so long as current BACT is applied (requiring that the tank be bottom- or submerged-fill and be painted white), and use of the tanks is only to support operation of the simple cycle turbines and associated equipment.
Default VOC emission rates of 0.01 lb/hr and 0.02 tpy should be used for both lube oil and diesel fuel tanks. An explanation of how these rates were derived follows. While a typical size for a diesel storage tank is 500 gal, the permit should not place a numerical limit on the size of the storage tanks, so long as tanks are installed only for use in operating and maintaining the turbines and associated emergency diesel engines.
B. Short Term Emissions A typical short-term emission rate can be calculated using the equation provided in TCEQ publication APDG 6250, "Estimating Short Term Emission Rates from Tanks", September 2014). Lmax = (average vapor molecular weight x vapor pressure / ideal gas constant of 80.273 x temperature Rankine) x maximum filling rate Average vapor molecular weight and vapor pressure are estimated using data in AP-42 Chapter 7, Table 7.1-2 for No. 2 Distillate Fuel Oil. The vapor pressure of 0.02 psia corresponds to 1 mmHg, and is a reasonable estimate of the vapor pressure of both diesel fuel and turbine oil. A worst case temperature and maximum filling rate of 95°F and 200 gal/hr (respectively) are assumed, giving the following: Lmax = [(130 lb/lb-mol x 0.02 psia) / ((80.273 psia x gal/lb-mol x ⁰R) x 555 ⁰R)] x 200 gal/hr = 0.012 lb/hr
C. Long-Term Emission Rates Standing and working losses are estimated following AP-42, Chapter 7, equations 1-2 and 1-29.
To estimate standing losses, the vapor space volume is conservatively assumed to equal 500 gal (the volume of the tank), and a stock vapor density of 0.00046 lb/ft3 is estimated based on an average temperature of 70°F and the vapor pressure and molecular weight values noted above. A vapor space expansion factor of 0.05 is determined by assuming that the tank paint is white and in good condition, and conservative figures of 30°R and 1800 Btu/ft2 are assumed for the daily temperature range and annual average solar insolation. The vented vapor saturation factor is assumed to be 1 (based on the maximum value of that variable). Total standing losses for this scenario are: Ls = (365 yr)(66.8 ft3)(0.00046 lb/ft3)(0.05)(1) = 0.6 lb/yr
To estimate working losses, the vapor pressure and molecular weight values noted above are used, and a total throughput of 5,000 gal is assumed. KN and KP values of 1 each are selected for fewer than 36 turnovers/yr and non-crude oil product. Lw = (0.001 lb-mol/psia x Bbl)(130 lb/lb-mol)(0.02 psia)(119 Bbl/yr)(1)(1) = 0.3 lb/yr
The total annual emissions is determined by adding the standing and working losses and is less than 0.01 tpy.
End of worksheet

## Tank–3
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Tank-3
This sheet details tank specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | TANK3 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Material stored |  | diesel or lube oil
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.01 | 0.02
This cell left intentionally blank.
V. Calculation Methodology
A. Overview Diesel and lube oil storage tanks maintained at a gas turbine installation, which are to be used exclusively in supplying diesel and lube oil to the turbine and emergency engines, have low overall capacities and throughputs. Considering that both diesel fuel and lube oil have low volatility, default emission rates are recommended for these sources. The default emission rates are expected to be representative so long as current BACT is applied (requiring that the tank be bottom- or submerged-fill and be painted white), and use of the tanks is only to support operation of the simple cycle turbines and associated equipment.
Default VOC emission rates of 0.01 lb/hr and 0.02 tpy should be used for both lube oil and diesel fuel tanks. An explanation of how these rates were derived follows. While a typical size for a diesel storage tank is 500 gal, the permit should not place a numerical limit on the size of the storage tanks, so long as tanks are installed only for use in operating and maintaining the turbines and associated emergency diesel engines.
B. Short Term Emissions A typical short-term emission rate can be calculated using the equation provided in TCEQ publication APDG 6250, "Estimating Short Term Emission Rates from Tanks", September 2014). Lmax = (average vapor molecular weight x vapor pressure / ideal gas constant of 80.273 x temperature Rankine) x maximum filling rate Average vapor molecular weight and vapor pressure are estimated using data in AP-42 Chapter 7, Table 7.1-2 for No. 2 Distillate Fuel Oil. The vapor pressure of 0.02 psia corresponds to 1 mmHg, and is a reasonable estimate of the vapor pressure of both diesel fuel and turbine oil. A worst case temperature and maximum filling rate of 95°F and 200 gal/hr (respectively) are assumed, giving the following: Lmax = [(130 lb/lb-mol x 0.02 psia) / ((80.273 psia x gal/lb-mol x ⁰R) x 555 ⁰R)] x 200 gal/hr = 0.012 lb/hr
C. Long-Term Emission Rates Standing and working losses are estimated following AP-42, Chapter 7, equations 1-2 and 1-29.
To estimate standing losses, the vapor space volume is conservatively assumed to equal 500 gal (the volume of the tank), and a stock vapor density of 0.00046 lb/ft3 is estimated based on an average temperature of 70°F and the vapor pressure and molecular weight values noted above. A vapor space expansion factor of 0.05 is determined by assuming that the tank paint is white and in good condition, and conservative figures of 30°R and 1800 Btu/ft2 are assumed for the daily temperature range and annual average solar insolation. The vented vapor saturation factor is assumed to be 1 (based on the maximum value of that variable). Total standing losses for this scenario are: Ls = (365 yr)(66.8 ft3)(0.00046 lb/ft3)(0.05)(1) = 0.6 lb/yr
To estimate working losses, the vapor pressure and molecular weight values noted above are used, and a total throughput of 5,000 gal is assumed. KN and KP values of 1 each are selected for fewer than 36 turnovers/yr and non-crude oil product. Lw = (0.001 lb-mol/psia x Bbl)(130 lb/lb-mol)(0.02 psia)(119 Bbl/yr)(1)(1) = 0.3 lb/yr
The total annual emissions is determined by adding the standing and working losses and is less than 0.01 tpy.
End of worksheet

## Tank–4
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Tank-4
This sheet details tank specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | TANK4 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Material stored |  | diesel or lube oil
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.01 | 0.02
This cell left intentionally blank.
V. Calculation Methodology
A. Overview Diesel and lube oil storage tanks maintained at a gas turbine installation, which are to be used exclusively in supplying diesel and lube oil to the turbine and emergency engines, have low overall capacities and throughputs. Considering that both diesel fuel and lube oil have low volatility, default emission rates are recommended for these sources. The default emission rates are expected to be representative so long as current BACT is applied (requiring that the tank be bottom- or submerged-fill and be painted white), and use of the tanks is only to support operation of the simple cycle turbines and associated equipment.
Default VOC emission rates of 0.01 lb/hr and 0.02 tpy should be used for both lube oil and diesel fuel tanks. An explanation of how these rates were derived follows. While a typical size for a diesel storage tank is 500 gal, the permit should not place a numerical limit on the size of the storage tanks, so long as tanks are installed only for use in operating and maintaining the turbines and associated emergency diesel engines.
B. Short Term Emissions A typical short-term emission rate can be calculated using the equation provided in TCEQ publication APDG 6250, "Estimating Short Term Emission Rates from Tanks", September 2014). Lmax = (average vapor molecular weight x vapor pressure / ideal gas constant of 80.273 x temperature Rankine) x maximum filling rate Average vapor molecular weight and vapor pressure are estimated using data in AP-42 Chapter 7, Table 7.1-2 for No. 2 Distillate Fuel Oil. The vapor pressure of 0.02 psia corresponds to 1 mmHg, and is a reasonable estimate of the vapor pressure of both diesel fuel and turbine oil. A worst case temperature and maximum filling rate of 95°F and 200 gal/hr (respectively) are assumed, giving the following: Lmax = [(130 lb/lb-mol x 0.02 psia) / ((80.273 psia x gal/lb-mol x ⁰R) x 555 ⁰R)] x 200 gal/hr = 0.012 lb/hr
C. Long-Term Emission Rates Standing and working losses are estimated following AP-42, Chapter 7, equations 1-2 and 1-29.
To estimate standing losses, the vapor space volume is conservatively assumed to equal 500 gal (the volume of the tank), and a stock vapor density of 0.00046 lb/ft3 is estimated based on an average temperature of 70°F and the vapor pressure and molecular weight values noted above. A vapor space expansion factor of 0.05 is determined by assuming that the tank paint is white and in good condition, and conservative figures of 30°R and 1800 Btu/ft2 are assumed for the daily temperature range and annual average solar insolation. The vented vapor saturation factor is assumed to be 1 (based on the maximum value of that variable). Total standing losses for this scenario are: Ls = (365 yr)(66.8 ft3)(0.00046 lb/ft3)(0.05)(1) = 0.6 lb/yr
To estimate working losses, the vapor pressure and molecular weight values noted above are used, and a total throughput of 5,000 gal is assumed. KN and KP values of 1 each are selected for fewer than 36 turnovers/yr and non-crude oil product. Lw = (0.001 lb-mol/psia x Bbl)(130 lb/lb-mol)(0.02 psia)(119 Bbl/yr)(1)(1) = 0.3 lb/yr
The total annual emissions is determined by adding the standing and working losses and is less than 0.01 tpy.
End of worksheet

## Tank–5
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Tank-5
This sheet details tank specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | TANK5 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Material stored |  | diesel or lube oil
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.01 | 0.02
This cell left intentionally blank.
V. Calculation Methodology
A. Overview Diesel and lube oil storage tanks maintained at a gas turbine installation, which are to be used exclusively in supplying diesel and lube oil to the turbine and emergency engines, have low overall capacities and throughputs. Considering that both diesel fuel and lube oil have low volatility, default emission rates are recommended for these sources. The default emission rates are expected to be representative so long as current BACT is applied (requiring that the tank be bottom- or submerged-fill and be painted white), and use of the tanks is only to support operation of the simple cycle turbines and associated equipment.
Default VOC emission rates of 0.01 lb/hr and 0.02 tpy should be used for both lube oil and diesel fuel tanks. An explanation of how these rates were derived follows. While a typical size for a diesel storage tank is 500 gal, the permit should not place a numerical limit on the size of the storage tanks, so long as tanks are installed only for use in operating and maintaining the turbines and associated emergency diesel engines.
B. Short Term Emissions A typical short-term emission rate can be calculated using the equation provided in TCEQ publication APDG 6250, "Estimating Short Term Emission Rates from Tanks", September 2014). Lmax = (average vapor molecular weight x vapor pressure / ideal gas constant of 80.273 x temperature Rankine) x maximum filling rate Average vapor molecular weight and vapor pressure are estimated using data in AP-42 Chapter 7, Table 7.1-2 for No. 2 Distillate Fuel Oil. The vapor pressure of 0.02 psia corresponds to 1 mmHg, and is a reasonable estimate of the vapor pressure of both diesel fuel and turbine oil. A worst case temperature and maximum filling rate of 95°F and 200 gal/hr (respectively) are assumed, giving the following: Lmax = [(130 lb/lb-mol x 0.02 psia) / ((80.273 psia x gal/lb-mol x ⁰R) x 555 ⁰R)] x 200 gal/hr = 0.012 lb/hr
C. Long-Term Emission Rates Standing and working losses are estimated following AP-42, Chapter 7, equations 1-2 and 1-29.
To estimate standing losses, the vapor space volume is conservatively assumed to equal 500 gal (the volume of the tank), and a stock vapor density of 0.00046 lb/ft3 is estimated based on an average temperature of 70°F and the vapor pressure and molecular weight values noted above. A vapor space expansion factor of 0.05 is determined by assuming that the tank paint is white and in good condition, and conservative figures of 30°R and 1800 Btu/ft2 are assumed for the daily temperature range and annual average solar insolation. The vented vapor saturation factor is assumed to be 1 (based on the maximum value of that variable). Total standing losses for this scenario are: Ls = (365 yr)(66.8 ft3)(0.00046 lb/ft3)(0.05)(1) = 0.6 lb/yr
To estimate working losses, the vapor pressure and molecular weight values noted above are used, and a total throughput of 5,000 gal is assumed. KN and KP values of 1 each are selected for fewer than 36 turnovers/yr and non-crude oil product. Lw = (0.001 lb-mol/psia x Bbl)(130 lb/lb-mol)(0.02 psia)(119 Bbl/yr)(1)(1) = 0.3 lb/yr
The total annual emissions is determined by adding the standing and working losses and is less than 0.01 tpy.
End of worksheet

## Tank–6
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Tank-6
This sheet details tank specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | TANK6 | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Material stored |  | diesel or lube oil
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.01 | 0.02
This cell left intentionally blank.
V. Calculation Methodology
A. Overview Diesel and lube oil storage tanks maintained at a gas turbine installation, which are to be used exclusively in supplying diesel and lube oil to the turbine and emergency engines, have low overall capacities and throughputs. Considering that both diesel fuel and lube oil have low volatility, default emission rates are recommended for these sources. The default emission rates are expected to be representative so long as current BACT is applied (requiring that the tank be bottom- or submerged-fill and be painted white), and use of the tanks is only to support operation of the simple cycle turbines and associated equipment.
Default VOC emission rates of 0.01 lb/hr and 0.02 tpy should be used for both lube oil and diesel fuel tanks. An explanation of how these rates were derived follows. While a typical size for a diesel storage tank is 500 gal, the permit should not place a numerical limit on the size of the storage tanks, so long as tanks are installed only for use in operating and maintaining the turbines and associated emergency diesel engines.
B. Short Term Emissions A typical short-term emission rate can be calculated using the equation provided in TCEQ publication APDG 6250, "Estimating Short Term Emission Rates from Tanks", September 2014). Lmax = (average vapor molecular weight x vapor pressure / ideal gas constant of 80.273 x temperature Rankine) x maximum filling rate Average vapor molecular weight and vapor pressure are estimated using data in AP-42 Chapter 7, Table 7.1-2 for No. 2 Distillate Fuel Oil. The vapor pressure of 0.02 psia corresponds to 1 mmHg, and is a reasonable estimate of the vapor pressure of both diesel fuel and turbine oil. A worst case temperature and maximum filling rate of 95°F and 200 gal/hr (respectively) are assumed, giving the following: Lmax = [(130 lb/lb-mol x 0.02 psia) / ((80.273 psia x gal/lb-mol x ⁰R) x 555 ⁰R)] x 200 gal/hr = 0.012 lb/hr
C. Long-Term Emission Rates Standing and working losses are estimated following AP-42, Chapter 7, equations 1-2 and 1-29.
To estimate standing losses, the vapor space volume is conservatively assumed to equal 500 gal (the volume of the tank), and a stock vapor density of 0.00046 lb/ft3 is estimated based on an average temperature of 70°F and the vapor pressure and molecular weight values noted above. A vapor space expansion factor of 0.05 is determined by assuming that the tank paint is white and in good condition, and conservative figures of 30°R and 1800 Btu/ft2 are assumed for the daily temperature range and annual average solar insolation. The vented vapor saturation factor is assumed to be 1 (based on the maximum value of that variable). Total standing losses for this scenario are: Ls = (365 yr)(66.8 ft3)(0.00046 lb/ft3)(0.05)(1) = 0.6 lb/yr
To estimate working losses, the vapor pressure and molecular weight values noted above are used, and a total throughput of 5,000 gal is assumed. KN and KP values of 1 each are selected for fewer than 36 turnovers/yr and non-crude oil product. Lw = (0.001 lb-mol/psia x Bbl)(130 lb/lb-mol)(0.02 psia)(119 Bbl/yr)(1)(1) = 0.3 lb/yr
The total annual emissions is determined by adding the standing and working losses and is less than 0.01 tpy.
End of worksheet

## Emergency Engine
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Emergency Engine
This sheet details emergency engine specifications and determines emission rates. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | EGEN | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 10 ft
Diameter (ft) |  | 0.32 ft
Temperature (°F) |  | 859 ⁰F
Velocity (fps) |  | 73.5 fps
This cell left intentionally blank.
III. Input Parameters
Parameter | Value | Maximum
Rated brake power of engine (hp) |  | 1234
This cell left intentionally blank.
IV. Project Emission Rates
Pollutant | Emission Factor | Emission Factor Unit | lb/hr | tpy
NOX | 4.56 | g/hp-hr | 0 | 0
CO | 2.62 | g/hp-hr | 0 | 0
PM | 0.16 | g/hp-hr | 0 | 0
PM10 | 0.16 | g/hp-hr | 0 | 0
PM2.5 | 0.16 | g/hp-hr | 0 | 0
VOC | 0.24 | g/hp-hr | 0 | 0
SO2 | 0.0049 | g/hp-hr | 0 | 0
This cell left intentionally blank.
V. Calculation Methodology
A. Short-term emissions (NOx, CO, PM, VOC) Emission rates are calculated based on EPA performance standards for non-road engines (40 CFR § 89.112), which are consistent with current BACT. The short-term emission rate is obtained by multiplying the engine's rated brake power by the appropriate emission factor, and then converting from grams to pounds. All particulate is assumed to be emitted as PM2.5. Emission rate = engine brake power x emission factor x (1 lb/453.6 g)
B. Short-term emissions (SO2) Emission rates are estimated based on the fuel consumption rate and the use of ultra-low sulfur diesel (ULSD), which contains at most 15 ppmw total sulfur. The fuel consumption rate depends on the design of the engine. A reasonable approximation for fuel consumption can be made by assuming an energy content of 137,000 Btu/gal for diesel fuel, a density of 7.1 lb/gal, and a brake-specific fuel consumption (BSFC) of 7,000 Btu/hp-hr (AP-42 Section 3.3. This equates to a thermal efficiency of approximately 36%.) Fuel consumption (gal/hr) = engine brake power x (1 gal/137,000 Btu) x (7.1 lb/gal) Emission rate = fuel consumption x engine brake power x (15 lb S/1,000,000 lb diesel) x (64 lb SO2/32 lb S)
C. Annual emissions Current BACT tracks MACT ZZZZ in limiting the engines to 100 hr/yr of non-emergency use. Therefore, annual emission rates for all pollutants can be determined by multiplying the short-term emission rate by 100 hr/yr and by 1 ton/2000 lb.
End of worksheet

## Fugitive Emissions
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Fugitive Emissions
This sheet details fugitive emission specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | FUG | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) |  | 3 ft
This cell left intentionally blank.
III. Project Emission Rates
Pollutant | lb/hr | tpy
VOC | 0.5 | 2.2
This cell left intentionally blank.
IV. Calculation Methodology
For an installation containing only simple cycle gas turbines and ancillary equipment, total VOC emissions from piping components are not large enough to warrant the use of a specific leak detection and repair (LDAR) program. Operators will use good practice for minimizing emissions. Piping components are either in natural gas or lube oil service. Estimates of piping fugitive emissions from recent permit applications indicate that uncontrolled emission rates are typically <0.01 lb/hr VOC for natural gas piping, and 0.3-1.0 lb/hr VOC for lube oil piping. Since accurate piping counts are normally not available at the time a permit application is filed, and the actual emission rate is insignificant, default emission rates of 0.5 lb/hr and 2.20 tpy VOC should be used. The default emission rates are expected to be representative so long as operators repair leaks in the lube oil circulation system as soon as practicable after they are discovered.
End of worksheet

## Maintenance Activities
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Maintenance Activities
This sheet details maintenance activity specifications and emission rates. The default emission rates below cannot be exceeded or increased with this RAP. Instructions: 1. Complete all information below.
This cell left intentionally blank.
I. General Information
Parameter | Value | Requirements
EPN | MAINT | NA
Zone |  | 13, 14, or 15
UTM Coordinate - Easting (meters) |  | Between 205,000 and 795,000
UTM Coordinate - Northing (meters) |  | Between 2,854,000 and 4,059,000
This cell left intentionally blank.
II. Discharge Parameters
Parameter | Value | Minimum
Release Height (ft) of filter and CEMS maintenance activities |  | 15 ft
Other maintenance activities included in MAINT do not have a minimum stack height requirement.
This cell left intentionally blank.
III. Project Emission Rates
Pollutant | lb/hr | tpy
NOx | <0.01 | 0.05
CO | <0.01 | 0.05
PM | 0.14 | 0.01
PM10 | 0.14 | 0.01
PM2.5 | 0.14 | 0.01
VOC | 0.1 | 0.2
This cell left intentionally blank.
IV. Calculation Methodology
A. Overview Various routine maintenance activities are required in order to keep a gas turbine in good working order. These activities generally do not create the potential for significant air emissions, and no control techniques are available other than general work practices for minimizing the formation of emissions. Additionally, accurate emission estimation methodologies are not available for most routine maintenance activities. Default emission rates are recommended for each activity, which are expected to be representative so long as the activities are carried out using good practice for minimizing emissions. Current practice in writing permits for simple cycle turbine installations is to list a general allowable emission rate that applies to all miscellaneous maintenance activities. Emissions from combustion of natural gas during start-up and shutdown of a turbine are assumed to be less than the rates occurring during normal operations at full load, and are therefore not addressed separately. Emission estimates for the following types of maintenance activities are discussed: replacement of inlet air system filters, water washing of turbine (on-line and off-line), fuel line venting, and CEMS calibration.
B. Replacement of Inlet Air System Filters Gas turbines are susceptible to fouling, corrosion, and abrasion of the compressor and turbine blades due to dust and other impurities in the intake air. An inlet air filtration system must therefore be used which removes impurities from the intake air to the maximum extent possible. Filters are periodically replaced to ensure that pressure drop due to the filtration system is reduced to acceptable levels. The particulate emission rate for filter change-outs depends on the total dust loading in the filter being replaced, but also on the procedure used to remove and dispose of the used filter. If the used filter is removed and disposed of in a manner that eliminates the release of visible emissions, then particulate emissions are not expected to be significant. A default emission rate of 0.1 lb/event particulate is recommended for filter change-outs that are conducted following the manufacturer's recommendations, and without the release of any visible emissions to the atmosphere.
C. Turbine Washing During operation of a gas turbine, particulate matter that is not removed by the inlet air filtration system causes fouling of the internal rotating blades, leading to increased frictional losses (due to increased blade surface roughness). In order to recover performance lost due to fouling, a typical turbine installation will employ a program of on-line and off-line washing of the gas turbine to remove fouling.
During on-line washing, water (or a water-detergent solution) is sprayed into the compression section of the gas turbine while the system is operating with a load. The water removes solid deposits on the compressor blades by dissolving them. Solid particles dissolved in the wash water are either redeposited on components in the turbine section or emitted to the atmosphere with the combustion exhaust gases. Therefore, particulate emissions from on-line washing are expected to be a function of the total mass of deposits removed from the turbine blades during a washing event. A typical method to estimate emissions for on-line washing is to estimate the total loading of deposits on the turbine blades (assuming that a uniform layer of dust coats a fraction of the total blade surface area), and then assume that all solids are removed and emitted as PM2.5. Due to the uncertainty in estimating the extent of coverage and the thickness of the fouling, this approach should be treated as yielding an order of magnitude estimate at best. A typical estimate assumes a total blade surface area of 2000 ft2, 5% of which is covered with a 5 µm layer of flue dust (density of 65 lb/ft 2). Assuming all of the dust is removed and eventually emitted with the combustion exhaust as PM2.5, the total emission rate is: Emission rate = 0.05(2000 ft2)(0.00005 m)(1 ft/0.3048 m)(65 lb/ft3) = 0.1 lb/event This value is small in comparison to the total amount of particulate formed from combustion. Since the contribution of particulate from on-line washing is not expected to interfere with compliance with the turbine's particulate emission limit, it can be disregarded.
For off-line washing, the gas turbine must be shut down and allowed to cool. It is then cranked while being sprayed with a detergent solution. After a certain period of soaking, the turbine is rinsed with water while cranking. Detergent solution and rinse water are drained to a sump and removed by vacuum truck. The primary source of air emissions during off-line washing is the evaporation of VOC contained in the detergent solution when this solution is drained to a sump or collected by a vacuum truck. Organic components of turbine cleaning detergents include glycol ethers and surfactants, which have relatively low vapor VOC vapor pressures. A representative emission rate can be estimated using AP-42, Section 5, equation 1. The usage rate and volatility of the cleaning solutions used in practice will vary, so this estimate should be treated as an order of magnitude estimate. Emission rate = 12.46 x [(saturation factor x vapor pressure x molecular weight)/temperature Rankine] The SDS for a common cleaning solution ("Zok 27") lists a vapor pressure of 0.6 kPa (0.09 psia) at 15°C and the manufacturer recommends that the solution be diluted with water at a ratio of 1:4 prior to use. Molecular weight data is not given. A rough estimate of the VOC vapor pressure of the diluted detergent is made by assuming the following: -The vapor pressure of the undiluted detergent is three times as high at 95°F as at 15°C (this is approximately true for water). -The detergent has liquid- and vapor-phase molecular weights equal to that of 2-Butoxyethanol (118 lb/lb-mol), a typical glycol ether. -The detergent has a density comparable to that of water. -The activity coefficient of the water-detergent mixture is 1. -The liquid phase mole fraction of the diluted detergent is approximately 4%, and its VOC va­por pressure is 0.04 x 3 x 0.09 which is about 0.01 psia. When the volume of liquid drained is 600 gal (a typical value from recent permit applications), total emissions of VOC are 0.02 lb/hr. This represents a reasonable default emission rate for off-line washing conducted using a low volatility detergent, where the sump is emptied into a closed container (i.e., a vacuum truck) as soon as practicable after the detergent solution is drained.
D. Inlet Fuel Line Venting During maintenance on the gas turbines, portions of the fuel gas delivery system may need to be evacuated. These fuel lines contain natural gas, which has only trace amounts of VOC. Control is not required for purging small quantities of natural gas to the air. Emissions are estimated using the ideal gas law, with a representative value for the isolated volume to be vented and the VOC content of the natural gas assumed. A default emission rate of 0.1lb/event is expected to be representative so long as fuel gas venting is limited to no more than that required to safely carry out maintenance activities on the turbine installation.
E. CEMS Calibration During calibration of the NOx and CO CEMS on a gas turbine, analytical gases of known concentration are introduced to the CEMS and emitted to the atmosphere. Worst-case values reported in recent permit applications indicate the use of 1 scf/min of calibration gas with a concentration of 1,000 ppmv of NOx or CO. For up to 10 calibration runs in an hour and 100 calibration events per year, the total mass emission rate would not exceed 0.01 lb/hr or 0.01 tpy.
End of worksheet

## BACT
Press UP or DOWN ARROW in column A to read through the document. Note: This worksheet is just text and has no input areas. The text is broken into multiple cells for ease of reading.
Best Available Control Technology
This sheet lists the practices and controls which represent Best Available Control Technology (BACT) for each specific unit in this project. BACT is required by 30 TAC §116.111(a)(2)(C). Instructions: 1. Review the BACT requirements. 2. Acceptance of the BACT for each unit is confirmed on the Emission Summary sheet.
This cell is left intentionally blank.
I. Simple Cycle Turbine
NOX: 9 parts per million by volume, dry basis (ppmvd) at 15% O2 during steady state operations using dry low NOX (DLN) burners. Installing a selective catalytic reduction (SCR) would not be economically reasonable given the limited annual operating hours.
CO: 9 ppmvd at 15% O2 using DLN and good combustion practices. An oxidation catalyst would not be economically reasonable given the limited annual operating hours.
VOC: 2.0 ppmvd at 15% O2 using good combustion practices, good burner design, and firing pipeline-quality natural gas.
SO2 and H2SO4: Firing pipeline-quality natural gas with a sulfur content not exceeding 2.0 grains total sulfur per 100 dry standard cubic feet (dscf) on an hourly basis, and 0.25 grains total sulfur per 100 dscf on an annual basis.
PM/PM10/PM2.5: Firing pipeline-quality natural gas and good combustion practices.
MSS: Conducted in accordance with manufacturer’s recommendations, minimizing the duration of the events (as required by the Special Conditions), and meeting the emission limitations on the maximum allowable emission rates table (MAERT).
This cell is left intentionally blank.
II. Fire Water Pump
Meeting the requirements of 40 CFR Part 60, Subpart IIII.
Firing ultra-low sulfur diesel fuel (no more than 15 parts per million (ppm) sulfur by weight).
Limited to 100 hrs/yr of non-emergency operation.
Have a non-resettable runtime meter.
This cell is left intentionally blank.
III. Dew Point Heater
Low NOX burners limited to 0.06 lb NOX / MMBtu (higher heating value (HHV) basis).
Firing pipeline-quality natural gas.
This cell is left intentionally blank.
IV. Lube Oil Vent
Lube oil mist shall be minimized through the use of a mist elimination system which is designed to achieve 99% or greater reduction of fine particulate matter (PM2.5).
This cell is left intentionally blank.
V. Tank
Painted white.
Submerged fill.
This cell is left intentionally blank.
VI. Emergency Engine
Meeting the requirements of 40 CFR Part 60, Subpart IIII.
Firing ultra-low sulfur diesel fuel (no more than 15 ppm sulfur by weight).
Limited to 100 hrs/yr of non-emergency operation.
Have a non-resettable runtime meter.
This cell is left intentionally blank.
VII. Fugitive Emissions
Repair leaks as soon as possible.
This cell is left intentionally blank.
VIII. Maintenance Activities
Limiting the duration of events.
Use good practices for minimizing emissions.
End of worksheet

## CND
There are no input areas on this worksheet. Press UP or DOWN ARROW in column A to read through the document.
Special Conditions
This sheet contains the draft Special Conditions prepared by the TCEQ for RAP-SCT projects. Instructions: 1. Review the Special Conditions. 2. Acceptance of the Special Conditions is confirmed on the Emission Summary sheet.
This cell is left intentionally blank.
1 | This permit authorizes emissions only from those emission points listed in the attached MAERT, and the facilities covered by this permit are authorized to emit subject to the emission rate limits on that table and other operating conditions specified in this permit. Also, this permit authorizes the emissions from planned MSS.
Federal Regulations
2 | The permitted sources at these facilities shall comply with all applicable requirements of the following federal regulations:
2 | A | The EPA NSPS in 40 CFR Part 60:
2 | A | (1) | Subpart A: General Provisions
2 | A | (2) | Subpart KKKK: Stationary Combustion Turbines
2 | A | (3) | Subpart IIII: Stationary Compression Ignition Internal Combustion Engines
2 | B | The EPA NESHAP for Source Categories in 40 CFR Part 63:
2 | B | (1) | Subpart A: General Provisions
2 | B | (2) | Subpart ZZZZ: Stationary Reciprocating Internal Combustion Engines
3 | If any condition of this permit is more stringent than the regulations so incorporated, then for the purposes of complying with this permit, the permit shall govern and be the standard by which compliance shall be demonstrated.
Operational Specifications
4 | Opacity of emissions from sources authorized by this permit shall not exceed 5 percent averaged over any six minute period. During periods of startup, shutdown or maintenance, the opacity from the stacks shall not exceed 15 percent over any six minute period.
4 | A | Visible emission observations shall be conducted each calendar quarter for each stack during normal operation, unless the emission unit is not operating for the entire calendar quarter. Observations shall be made at least 15 feet and no more than 0.25 miles from the emission points. Up to three emissions points may be read concurrently, provided that all three emission points are within a 70 degree viewing sector in front of the observer and the sun is positioned at the observer's back.
4 | B | If visible emissions are observed from the stack(s), then opacity shall be determined by EPA Reference Method 9 within 24 hours of observing visible emissions. Contributions from uncombined water shall not be included in determining compliance with this condition.
4 | C | If the opacity limits of this Special Condition are exceeded, corrective action to eliminate the source of visible emissions shall be taken promptly and documented within one week of first observation.
5 | Upon request by the Executive Director of the TCEQ or any local air pollution control program having jurisdiction, the permit holder shall provide a sample and/or an analysis of the fuel fired in the gas turbines or engines, or shall allow an air pollution control agency representative to obtain a sample for analysis.
6 | Fuel for each turbine shall be pipeline-quality natural gas containing no more than 2.0 grains total sulfur per 100 dscf on an hourly basis, and 0.25 grains total sulfur per 100 dscf on an annual basis.
7 | Each turbine shall be limited to 2500 hours of operation per year, including periods of MSS.
8 | Exhaust gases from each turbine shall not exceed the following concentrations in ppmvd at 15 percent O2:
8 | NOx | NOx | 9.0 on a 3-hour rolling average
8 | CO | CO | 9.0 on a 3-hour rolling average
8 | VOC | VOC | 2.0 on a 3-hour rolling average
8 | A | Each turbine’s normal operating range is from 60 to 100 percent of base load except for periods of planned MSS.
8 | B | Reduced load operation below base load not associated with planned MSS is authorized and not subject to the above concentration limits, provided the emission rates specified in the MAERT are not exceeded.
8 | C | Planned startup events for each turbine are excluded from the above concentration limits. Each startup event shall not exceed one hour and is defined as the period that begins when an initial flame detection signal is recorded in the plant’s DAHS and ends when the turbine enters lean pre-mix operating mode.
8 | D | Planned shutdown events for each turbine are excluded from the above concentration limits. Each shutdown event shall not exceed one hour and is defined as the period that begins when the DAHS received a shutdown signal and exits the lean pre-mix operating mode and ends when the flame detection signal is no longer detected by the plant’s DAHS.
8 | E | Emissions from maintenance activities (Attachment A) shall be excluded. Compliance shall be demonstrated by comparing the pollutant’s total hourly emissions as calculated or measured by the CEMS to the hourly MSS rates listed in the MAERT. The permit holder shall sum all emissions from planned maintenance activities on a rolling 12-month basis for each EPN to demonstrate compliance with the MAERT.
9 | Each dew point heater shall be designed to emit no more than 0.06 lb/MMBtu NOx (HHV basis) fuel fired on a 1-hour block average.
10 | The following requirements apply to each engine:
10 | A | Fuel for each engine shall be limited to ULSD containing no more than 15 ppmw total sulfur.
10 | B | Each engine shall be limited to 100 hours per year during non-emergency situations.
10 | C | Each engine shall be equipped with a non-resettable hour meter.
Initial Determination of Compliance
11 | Sampling ports and platforms shall be incorporated into the design of the turbine exhaust stacks according to the specifications set forth in the TCEQ “Guidelines for Stack Sampling Facilities”. Alternate sampling facility designs may be submitted for approval by the TCEQ Regional Director. The permit holder shall perform stack sampling and other testing as required to establish the actual quantities of air contaminants being emitted into the atmosphere from each gas turbine. The permit holder is responsible for providing sampling and testing facilities and conducting the sampling and testing operations at his expense. Sampling shall be conducted in accordance with the appropriate procedures of the TCEQ Sampling Procedures Manual and EPA Reference Methods. The TCEQ Executive Director or his designated representative shall be afforded the opportunity to observe all such sampling upon request.
11 | Fuel sampling using the methods and procedures of 40 CFR § 60.4415 may be conducted in lieu of stack sampling for SO2 or the permit holder may be exempted from fuel monitoring of SO2 as provided under 40 CFR § 60.4365. If fuel sampling is used, compliance with NSPS Subpart KKKK SO2 limits shall be based on 100 percent conversion of the sulfur in the fuel to SO2. Any deviations from those procedures must be approved by the Executive Director of the TCEQ prior to sampling. Fuel sampling using the methods and procedures of 40 CFR § 60.4360 may be conducted in lieu of stack testing for SO2.
11 | A | The appropriate TCEQ Regional Office shall be contacted as soon as testing is scheduled but not less than 45 days prior to sampling to schedule a pre-test meeting. The notice shall include:
11 | A | (1) | Proposed date for pre-test meeting.
11 | A | (2) | Date sampling will occur.
11 | A | (3) | Name of firm conducting sampling.
11 | A | (4) | Type of sampling equipment to be used.
11 | A | (5) | Method or procedure to be used in sampling.
11 | A | (6) | Procedure used to determine turbine load during and after the sampling period.
11 | A | A written proposed description of any deviation from sampling procedures specified in permit conditions or the TCEQ or EPA sampling procedures shall be made available to the TCEQ prior to the pre-test meeting. The TCEQ Regional Director shall approve or disapprove of any deviation from specified sampling procedures.
11 | B | Air contaminants and diluents from the turbine to be sampled and analyzed include NOx, CO, PM, VOC, SO2, opacity, and O2. Fuel sampling using the methods and procedures of the applicable NSPS may be conducted in lieu of stack sampling for SO2.
11 | C | Each turbine shall be tested at a minimum and maximum load of the permitted operating range that is defined in this permit for the atmospheric conditions which exist during testing. Each tested load shall be identified in the sampling report. The permit holder shall present at the pre-test meeting the manner in which stack sampling will be executed in order to demonstrate compliance with emission standards found in 40 CFR Part 60, Subpart KKKK for combustion gas turbines.
11 | D | Test waivers and alternate or equivalent procedure proposals which must have EPA approval shall be submitted to the TCEQ Air Permits Division.
11 | E | Sampling shall occur within 60 days after achieving the maximum operating rate, but no later than 180 days after initial startup of the facilities and at other times when required by the TCEQ Regional Director. Requests for additional time to perform sampling shall be submitted to the appropriate regional office.
11 | F | Copies of the final sampling report shall be forwarded to the TCEQ within 60 days after sampling is completed. Sampling reports, including distribution instructions, shall comply with Chapter 14 of the TCEQ Sampling Procedures Manual.
Continuous Demonstration of Compliance
12 | The permit holder shall install, calibrate, and maintain a CEMS to measure and record the in-stack concentration of NOx, CO, and diluent gases (CO2 or O2) from each gas turbine stack.
12 | A | The NOx and diluent gas CEMS shall meet the design and performance specifications, pass the field tests, and meet the installation requirements and the data analysis and reporting requirements specified in the applicable Performance Specification Nos. 2 and 3, 40 CFR Part 60, Appendix B. The permit holder shall assure that the CEMS meets the applicable quality-assurance requirements specified in 40 CFR Part 60, Appendix F, Procedure 1.
12 | B | Compliance with the CEMS requirements of 40 CFR Part 60 can be demonstrated by meeting the applicable requirements of 40 CFR Part 75 provided that the holder of this permit demonstrates compliance with all applicable 40 CFR Part 60 emission standards.
12 | C | The CO CEMS shall meet the design and performance specifications, pass the field tests, and meet the installation requirements and the data analysis and reporting requirements specified in the applicable performance specifications in 40 CFR Part 60, Appendix B, Performance Specification No. 4.
12 | D | All CEMS shall meet the applicable quality assurance requirements specified in 40 CFR Part 60, Appendix F, except that CGA conducted in all four quarters may be used in lieu of the annual relative accuracy test audit. Quarterly CGAs shall be conducted at least 60 days apart. Relative accuracy exceedances (as specified in 40 CFR 60, Appendix F), CGA exceedances of ±15 percent accuracy, and any CEMS downtime shall be reported to the TCEQ regional office, and necessary corrective action shall be taken. Supplemental stack sampling may be required at the discretion of the TCEQ Regional Director.
12 | E | If any emission monitor fails to meet specified performance, it shall be repaired or replaced immediately. If repair or replacement is not immediately feasible, the monitor shall be repaired or replaced no later than seven days after the failure is first detected by an employee at the site, unless written permission is obtained from the TCEQ Regional Office which allows for longer repair/replacement time. The holder of this permit shall develop an operation and maintenance program (including stocking necessary spare parts) to ensure that the continuous monitors are available as required. A monitor with downtime due to breakdown or repair of more than 10 percent of the facility operating time for any calendar year will be considered as a defective monitor and the monitor must be replaced within two weeks after exceeding the 10 percent threshold.
12 | F | The monitoring data shall be reduced to hourly average values at least once every day, using a minimum of four equally-spaced data points from each one-hour period. At least two valid data points shall be generated during the hourly period in which zero and span is performed. The individual average concentrations shall be reduced to units of lbs/hr at least once every day.
12 | G | The monitoring data and quality-assurance data shall be maintained by the permit holder at the facility site. The data from the CEMS will be used to determine compliance with the conditions of this permit. During periods where the CEMS data is unavailable or not quality assured, compliance may alternatively be determined by using manufacturer emission factors or valid and representative data previously measured and recorded by the unit’s CEMS under similar operating conditions.
12 | H | The TCEQ Regional Office shall be notified at least 21 days prior to any required relative accuracy test audit, and Regional Office personnel shall be provided with an opportunity to observe the testing.
12 | I | If applicable, the requirements of 40 CFR Part 75, Appendices A and B, may be used as an alternative to the performance specifications and quality assurance requirements (respectively) of 40 CFR Part 60 for the NOx and O2 CEMS.
13 | The holder of this permit shall either measure, or develop a program to calculate, the total mass flow rate through the stacks to ensure continuous compliance with the emission limitations specified in the MAERT. The permit holder shall calculate hourly mass emissions in lbs/hr using the measured or calculated exhaust flow rate and the measured concentrations of NOx and CO from the CEMS required in this permit.
14 | The permit holder shall monitor fuel consumption from each gaseous fuel combustion device individually and continuously, using monitoring devices that are accurate to ±2.0 percent of the unit’s maximum flow and maintain, calibrate, and operate the devices in accordance with the manufacturer’s specifications. The devices shall be calibrated in accordance with the manufacturer’s recommendations or at least annually.
15 | After the initial demonstration of compliance, ongoing compliance with the VOC and PM tons per year emission rates in the MAERT shall be demonstrated by calculating rolling 12-month annual emissions from emission factors (lb/MMBtu, HHV) obtained from the results of the sampling required by this permit and the monthly total heat input (MMBtu, HHV) from natural gas fuel.
Recordkeeping Requirements
16 | The following records (written or electronic) shall be kept at the plant for the life of the permit. All records required in this permit shall be made available at the request of personnel from the TCEQ, EPA, or any local air pollution control program having jurisdiction:
16 | A | A copy of this permit.
16 | B | The initial permit application and subsequent representations submitted to the TCEQ.
16 | C | A complete copy of the testing reports and records of the initial performance testing completed to demonstrate initial compliance.
16 | D | Stack sampling results or other air emissions testing (other than CEMS data).
17 | The following records shall be maintained by the holder of this permit in a form suitable for inspection for a period of five years after collection and shall be made available upon request to representatives of the TCEQ, EPA, or any local air pollution control program having jurisdiction:
17 | A | The CEMS data to demonstrate compliance with the emission rates listed in the Special Conditions and the MAERT.
17 | B | Raw data files of all CEMS data including calibration checks and adjustments and maintenance performed on these systems in a permanent form suitable for inspection.
17 | C | Records for the hourly calculated values required to determine mass flow rates from CEMS data and compliance with the MAERT shall be cumulatively added during each hour of the month and stored electronically.
17 | D | Records of the hours of operation and the quantity of natural gas fired in the gas turbines.
17 | E | Records of dates and times for startups and shutdowns of each turbine.
17 | F | Records of fuel sampling conducted pursuant to 40 CFR Part 60, Subpart KKKK.
17 | G | Records of fuel delivery including sulfur content based on receipts or chemical analyses. Fuel designated as ULSD on the receipt is acceptable.
17 | H | Record of visible emissions or opacity observations, including corrective actions taken.
17 | I | Records of planned maintenance activities.
Attachment A - Maintenance Activities
The following list of maintenance activities is authorized by this permit. This list is not intended to be all-inclusive of activities at the site.
Planned Maintenance Activity |  |  |  | EPN | NOx | CO | VOC | PM | SO2
Combustion optimization* |  |  |  | CTG1 and/or CTG2 | X | X | X | X | X
Turbine washing online** |  |  |  | CTG1 and/or CTG2 | not selected | not selected | not selected | X | not selected
Miscellaneous particulate filter*** maintenance*** |  |  |  | MAINT | not selected | not selected | not selected | X | not selected
Gaseous fuel venting**** |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Water-based washing |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Management of sludge from pits, ponds, sumps, and water conveyances***** |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Organic chemical usage |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Inspection, repair, replacement, adjusting, testing, and calibration of analytical equipment, process instruments including sight glasses, meters, gauges, CEMS, or PEMS |  |  |  | MAINT | X | X | X | not selected | not selected
Small equipment and fugitive component repair and replacement in VOC service****** |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Maintenance of storage vessels storing materials with a vapor pressure <0.5 psia |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Maintenance of storage vessels storing gasoline of other materials with a vapor pressure > 0.5 psia |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Maintenance of storage vessels storing gasoline of other materials with a vapor pressure > 0.5 psia that require clearing of the vessels to allow for entry of personnel |  |  |  | MAINT | not selected | not selected | X | not selected | not selected
Notes
*Includes, but is not limited to, (1) leak or operability checks (e.g. turbine over-speed test, troubleshooting), (ii) balancing, and (iii) tuning activities that occur during seasonal tuning or after completion of initial construction, combustor change-out, major repair, combustor maintenance, or other similar circumstances.
**Involves the use of water only.
***Includes, but is not limited to, process-related building air filters, and combustion turbine air intake filters.
****Includes, but is not limited to, venting prior to pipeline pigging and meter proving.
*****Includes, but is not limited to, management by vacuum truck/dewatering of materials in open pits, ponds, sumps, tanks, and other closed/open vessels. Material include water and sludge materials containing miscellaneous VOCs such as diesel, lube oil, and other waste oils.
******Includes, but is not limited to, (i) repair/replacement of pumps, compressors, valves, pipes, flanges, transport lines, filters, and screens in natural gas, diesel oil, lube oil, and gasoline service, (ii) vehicle and mobile equipment maintenance that may involve VOC emissions, such as oil changes, transmission service, and hydraulic system service.
Acronyms
40 CFR |  | Title 40 Code of Federal Regulations
CEMS |  | Continuous Emissions Monitoring System
CGA |  | cylinder gas audits
CO |  | carbon monoxide
CO2 |  | carbon dioxide
DAHS |  | data acquisition and handling system
dscf |  | dry standard cubic feet
EPA |  | U.S. Environmental Protection Agency
EPN |  | emission point number
HHV |  | higher heating value
lb/MMBtu |  | pound per million British thermal units
lbs/hr |  | pounds per hour
MAERT |  | Maximum Allowable Emission Rates Table
MSS |  | maintenance, startup, and shutdown
NESHAP |  | National Emission Standards for Hazardous Air Pollutants
NOx |  | nitrogen oxides
NSPS |  | New Stationary Sources
O2 |  | oxygen
PEMS |  | Periodic Emissions Monitoring System
PM |  | particulate matter
ppmvd |  | parts per million by volume, dry basis
ppmw |  | parts per million by weight
psia |  | pounds per square inch absolute
SO2 |  | sulfur dioxide
TCEQ |  | Texas Commission on Environmental Quality
ULSD |  | ultra-low sulfur diesel
VOC |  | volatile organic compounds
End of worksheet

## Public Notice
Press TAB to move input areas. Press UP or DOWN ARROW in column A to read through the document.
Public Notice Applicability, Required Information, and Small Business Classification
This sheet is intended to assist in the determination of public notice requirements and is not a replacement for 30 TAC Chapter 39 (Public Notice). The THSC §382.056 and corresponding rules in 30 TAC Chapter 39 (Public Notice) require that you publish a notice of intent to obtain a permit and in certain circumstances, notice of preliminary decision. Notices must be published in a newspaper of general circulation in the municipality where the proposed facility is or will be located (not applicable to alternative language notices). The notices must include a description of the facility and the fact that a person who may be affected by emissions from the facility may request a public hearing and any other information the TCEQ requires by rule. Signs must also be posted at the site in compliance with 30 TAC Chapter §39.604(c). Additional information regarding public notice such as an overview of requirements, an applicability table, and a list of some common errors that may cause renotice and delays in processing your application can be found at:
www.tceq.texas.gov/permitting/air/bilingual/how1_2_pn.html
Instructions: 1. Complete all sections. 2. Complete all questions in the Small Business Classification section to determine eligibility.
This cell intentionally left blank
I. Public Notice Applicability
Is this an application for a new minor permit? | Yes
Is public notice required for this project as represented in this workbook? | Yes
Pollutants: | NOx, CO, PM, PM10, PM2.5, VOC, SO2, H2SO4
This cell intentionally left blank
II. Public Notice Information
A. Contact Information
Enter the contact information for the person responsible for publishing. This is a designated representative who is responsible for ensuring public notice is properly published in the appropriate newspaper and signs are posted at the facility site. This person will be contacted directly when the TCEQ is ready to authorize public notice for the application.
Prefix (Mr, Ms, Dr, etc.):
First Name:
Last Name:
Title:
Company Name:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
Enter the contact information for the Technical Contact. This is the designated representative who will be listed in the public notice as a contact for additional information.
Prefix (Mr, Ms, Dr, etc.):
First Name:
Last Name:
Title:
Company Name:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
B. Public place Place a copy of the full application (including all of this workbook and all attachments) at a public place in the county where the facilities are or will be located. You must state where in the county the application will be available for public review and comment. The location must be a public place and described in the notice. A public place is a location which is owned and operated by public funds (such as libraries, county courthouses, city halls) and cannot be a commercial enterprise. You are required to pre-arrange this availability with the public place indicated below. The application must remain available from the first day of publication through the designated comment period. If the application is submitted to the agency with information marked as Confidential, you are required to indicate which specific portions of the application are not being made available to the public. These portions of the application must be accompanied with the following statement: Any request for portions of this application that are marked as confidential must be submitted in writing, pursuant to the Public Information Act, to the TCEQ Public Information Coordinator, MC 197, P.O. Box 13087, Austin, Texas 78711-3087.
Name of Public Place:
Physical Address:
Address Line 2:
City:
ZIP Code:
County:
Has the public place granted authorization to place the application for public viewing and copying?
C. Alternate Language Publication In some cases, public notice in an alternate language is required. If an elementary or middle school nearest to the facility is in a school district required by the Texas Education Code to have a bilingual program, a bilingual notice will be required. If there is no bilingual program required in the school nearest the facility, but children who would normally attend those schools are eligible to attend bilingual programs elsewhere in the school district, the bilingual notice will also be required. If it is determined that alternate language notice is required, you are responsible for ensuring that the publication in the alternate language is complete and accurate in that language.
Is a bilingual program required by the Texas Education Code in the School District?
Are the children who attend either the elementary school or the middle school closest to your facility eligible to be enrolled in a bilingual program provided by the district?
If yes to either question above, list which language(s) are required by the bilingual program?
Enter second language if applicable
Enter third language if applicable
Enter fourth language if applicable
This cell intentionally left blank
III. Small Business Classification
Complete this section to determine small business classification. If a small business requests a permit, agency rules [30 TAC § 39.603(d)(1)(A)] allow for alternative public notification requirements if all of the following criteria are met. If these requirements are met, public notice does not have to include publication of the prominent (12 square inch) newspaper notice.
Does the company (including parent companies and subsidiary companies) have fewer than 100 employees or less than $6 million in annual gross receipts?
Is the site a major source under 30 TAC Chapter 122, Federal Operating Permit Program?
Are the site emissions of any individual air contaminant greater than or equal to 50 tpy?
Are the site emissions of all air contaminants combined greater than or equal to 75 tpy?
Small business classification:
This cell intentionally left blank
IV. Plain Language Summary
Applications deemed administratively complete by May 1, 2022 must provide a plain language summary of the application to be posted on the TCEQ website. Templates can be found at the link below.
https://www.tceq.texas.gov/permitting/air/guidance/newsourcereview/nsrapp-tools.html
Is a Plain Language Summary as required by 30 TAC § 39.405(k) provided with the application?
Is a Plain Language Summary in an alternative language as required by 30 TAC § 39.426(c) provided with the application?
End of worksheet

## Emission Summary
Emission Summary
This sheet provides summaries of the proposed project emissions and the electronic signature of agreement. Instructions: 1. The proposed emission rates for each source are automatically populated from the data entered on previous sheets. 2. Do not proceed if any total or emission rate displays "Error". Revise representations on the unit sheets. 3. Confirm agreement with the statement at the bottom of this sheet by electronically signing your name.
Emission Point No. | Source Name | NOx lb/hr | NOx tpy | CO lb/hr | CO tpy | PM lb/hr | PM tpy | PM10 lb/hr | PM10 tpy | PM2.5 lb/hr | PM2.5 tpy | VOC lb/hr | VOC tpy | SO2 lb/hr | SO2 tpy | H2SO4 lb/hr | H2SO4 tpy
| Total |  |  |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0
I have reviewed and agree to the following: the BACT as represented in this workbook; all emission rates represented in this workbook; the draft permit’s Special Conditions in this workbook; and the applicable air quality analysis report. In addition, this workbook is submitted as part of my application and accurately represents my proposed project.
Confirm that you agree with the statement above by electronically signing (typing) your name here:
End of worksheet

## Counties (hidden)
Rank | Name | NA Threshold Nox and VOC (TPY) | NA Threshold PM10 (TPY) | Distance to Property Line | Facility is within nonattainment area: | HGB Counties | Facility in HGB? | HGB > 10 Nox TYP? | CAP and Trade | Max Distance | Zones
1 | Anderson | 249 | 249 | 150 | FALSE | Harris | FALSE | TRUE | FALSE | #N/A | 13 | 40 CFR | in Title 40 Code of Federal Regulations
2 | Andrews | 249 | 249 | 150 |  | Chambers |  |  |  |  | 14 | CEMS | Continuous Emissions Monitoring System
3 | Angelina | 249 | 249 | 150 |  | Fort Bend |  |  |  |  | 15 | CGA | cylinder gas audits
4 | Aransas | 249 | 249 | 150 |  | Liberty | [5 empty] | CO | carbon monoxide
5 | Archer | 249 | 249 | 150 |  | Montgomery | [5 empty] | CO2 | carbon dioxide
6 | Armstrong | 249 | 249 | 150 |  | Waller | [5 empty] | DAHS | data acquisition and handling system
7 | Atascosa | 249 | 249 | 150 |  | Galveston | [5 empty] | dscf | dry standard cubic feet
8 | Austin | 249 | 249 | 150 |  | Brazoria | [5 empty] | EPA | U.S. Environmental Protection Agency
9 | Bailey | 249 | 249 | 150 | [7 empty] | EPN | emission point number
10 | Bandera | 249 | 249 | 150 | [7 empty] | HHV | higher heating value
11 | Bastrop | 249 | 249 | 150 | [7 empty] | lb/MMBtu | pound per million British thermal units
12 | Baylor | 249 | 249 | 150 | [7 empty] | lbs/hr | pounds per hour
13 | Bee | 249 | 249 | 150 | [7 empty] | MAERT | Maximum Allowable Emission Rates Table
14 | Bell | 249 | 249 | 150 | [7 empty] | MSS | maintenance, startup, and shutdown
15 | Bexar | 249 | 249 | 150 | [7 empty] | NESHAP | National Emission Standards for Hazardous Air Pollutants
16 | Blanco | 249 | 249 | 150 | [7 empty] | NOx | nitrogen oxides
17 | Borden | 249 | 249 | 150 | [7 empty] | NSPS | New Stationary Sources
18 | Bosque | 249 | 249 | 150 | [7 empty] | O2 | oxygen
19 | Bowie | 249 | 249 | 150 | [7 empty] | PEMS | Periodic Emissions Monitoring System
20 | Brazoria | 50 | 249 | 150 | [7 empty] | PM | particulate matter
21 | Brazos | 249 | 249 | 150 | [7 empty] | ppmvd | parts per million by volume, dry basis
22 | Brewster | 249 | 249 | 150 | [7 empty] | ppmw | parts per million by weight
23 | Briscoe | 249 | 249 | 150 | [7 empty] | psia | pounds per square inch absolute
24 | Brooks | 249 | 249 | 150 | [7 empty] | SO2 | sulfur dioxide
25 | Brown | 249 | 249 | 150 | [7 empty] | TCEQ | Texas Commission on Environmental Quality
26 | Burleson | 249 | 249 | 150 | [7 empty] | ULSD | ultra-low sulfur diesel
27 | Burnet | 249 | 249 | 150 | [7 empty] | VOC | volatile organic compounds
28 | Caldwell | 249 | 249 | 150
29 | Calhoun | 249 | 249 | 150
30 | Callahan | 249 | 249 | 150
31 | Cameron | 249 | 249 | 150
32 | Camp | 249 | 249 | 150
33 | Carson | 249 | 249 | 150
34 | Cass | 249 | 249 | 150
35 | Castro | 249 | 249 | 150
36 | Chambers | 50 | 249 | 150
37 | Cherokee | 249 | 249 | 150
38 | Childress | 249 | 249 | 150
39 | Clay | 249 | 249 | 150
40 | Cochran | 249 | 249 | 150
41 | Coke | 249 | 249 | 150
42 | Coleman | 249 | 249 | 150
43 | Collin | 50 | 249 | 150
44 | Collingsworth | 249 | 249 | 150
45 | Colorado | 249 | 249 | 150
46 | Comal | 249 | 249 | 150
47 | Comanche | 249 | 249 | 150
48 | Concho | 249 | 249 | 150
49 | Cooke | 249 | 249 | 150
50 | Coryell | 249 | 249 | 150
51 | Cottle | 249 | 249 | 150
52 | Crane | 249 | 249 | 150
53 | Crockett | 249 | 249 | 150
54 | Crosby | 249 | 249 | 150
55 | Culberson | 249 | 249 | 150
56 | Dallam | 249 | 249 | 150
57 | Dallas | 50 | 249 | 150
58 | Dawson | 249 | 249 | 150
59 | Deaf Smith | 249 | 249 | 150
60 | Delta | 249 | 249 | 150
61 | Denton | 50 | 249 | 150
62 | DeWitt | 249 | 249 | 150
63 | Dickens | 249 | 249 | 150
64 | Dimmit | 249 | 249 | 150
65 | Donley | 249 | 249 | 150
66 | Duval | 249 | 249 | 150
67 | Eastland | 249 | 249 | 150
68 | Ector | 249 | 249 | 150
69 | Edwards | 249 | 249 | 150
70 | Ellis | 50 | 249 | 150
71 | El Paso | 249 | 100 | 300
72 | Erath | 249 | 249 | 150
73 | Falls | 249 | 249 | 150
74 | Fannin | 249 | 249 | 150
75 | Fayette | 249 | 249 | 150
76 | Fisher | 249 | 249 | 150
77 | Floyd | 249 | 249 | 150
78 | Foard | 249 | 249 | 150
79 | Fort Bend | 50 | 249 | 150
80 | Franklin | 249 | 249 | 150
81 | Freestone | 249 | 249 | 150
82 | Frio | 249 | 249 | 150
83 | Gaines | 249 | 249 | 150
84 | Galveston | 50 | 249 | 150
85 | Garza | 249 | 249 | 150
86 | Gillespie | 249 | 249 | 150
87 | Glasscock | 249 | 249 | 150
88 | Goliad | 249 | 249 | 150
89 | Gonzales | 249 | 249 | 150
90 | Gray | 249 | 249 | 150
91 | Grayson | 249 | 249 | 150
92 | Gregg | 249 | 249 | 150
93 | Grimes | 249 | 249 | 150
94 | Guadalupe | 249 | 249 | 150
95 | Hale | 249 | 249 | 150
96 | Hall | 249 | 249 | 150
97 | Hamilton | 249 | 249 | 150
98 | Hansford | 249 | 249 | 150
99 | Hardeman | 249 | 249 | 150
100 | Hardin | 249 | 249 | 150
101 | Harris | 50 | 249 | 420
102 | Harrison | 249 | 249 | 150
103 | Hartley | 249 | 249 | 150
104 | Haskell | 249 | 249 | 150
105 | Hays | 249 | 249 | 150
106 | Hemphill | 249 | 249 | 150
107 | Henderson | 249 | 249 | 150
108 | Hidalgo | 249 | 249 | 150
109 | Hill | 249 | 249 | 150
110 | Hockley | 249 | 249 | 150
111 | Hood | 249 | 249 | 150
112 | Hopkins | 249 | 249 | 150
113 | Houston | 249 | 249 | 150
114 | Howard | 249 | 249 | 150
115 | Hudspeth | 249 | 249 | 150
116 | Hunt | 249 | 249 | 150
117 | Hutchinson | 249 | 249 | 150
118 | Irion | 249 | 249 | 150
119 | Jack | 249 | 249 | 150
120 | Jackson | 249 | 249 | 150
121 | Jasper | 249 | 249 | 150
122 | Jeff Davis | 249 | 249 | 150
123 | Jefferson | 249 | 249 | 150
124 | Jim Hogg | 249 | 249 | 150
125 | Jim Wells | 249 | 249 | 150
126 | Johnson | 50 | 249 | 150
127 | Jones | 249 | 249 | 150
128 | Karnes | 249 | 249 | 150
129 | Kaufman | 50 | 249 | 150
130 | Kendall | 249 | 249 | 150
131 | Kenedy | 249 | 249 | 150
132 | Kent | 249 | 249 | 150
133 | Kerr | 249 | 249 | 150
134 | Kimble | 249 | 249 | 150
135 | King | 249 | 249 | 150
136 | Kinney | 249 | 249 | 150
137 | Kleberg | 249 | 249 | 150
138 | Knox | 249 | 249 | 150
139 | Lamar | 249 | 249 | 150
140 | Lamb | 249 | 249 | 150
141 | Lampasas | 249 | 249 | 150
142 | La Salle | 249 | 249 | 150
143 | Lavaca | 249 | 249 | 150
144 | Lee | 249 | 249 | 150
145 | Leon | 249 | 249 | 150
146 | Liberty | 50 | 249 | 150
147 | Limestone | 249 | 249 | 150
148 | Lipscomb | 249 | 249 | 150
149 | Live Oak | 249 | 249 | 150
150 | Llano | 249 | 249 | 150
151 | Loving | 249 | 249 | 150
152 | Lubbock | 249 | 249 | 150
153 | Lynn | 249 | 249 | 150
154 | McCulloch | 249 | 249 | 150
155 | McLennan | 249 | 249 | 150
156 | McMullen | 249 | 249 | 150
157 | Madison | 249 | 249 | 150
158 | Marion | 249 | 249 | 150
159 | Martin | 249 | 249 | 150
160 | Mason | 249 | 249 | 150
161 | Matagorda | 249 | 249 | 150
162 | Maverick | 249 | 249 | 150
163 | Medina | 249 | 249 | 150
164 | Menard | 249 | 249 | 150
165 | Midland | 249 | 249 | 150
166 | Milam | 249 | 249 | 150
167 | Mills | 249 | 249 | 150
168 | Mitchell | 249 | 249 | 150
169 | Montague | 249 | 249 | 150
170 | Montgomery | 50 | 249 | 150
171 | Moore | 249 | 249 | 150
172 | Morris | 249 | 249 | 150
173 | Motley | 50 | 249 | 150
174 | Nacogdoches | 249 | 249 | 150
175 | Navarro | 249 | 249 | 150
176 | Newton | 249 | 249 | 150
177 | Nolan | 249 | 249 | 150
178 | Nueces | 249 | 249 | 150
179 | Ochiltree | 249 | 249 | 150
180 | Oldham | 249 | 249 | 150
181 | Orange | 249 | 249 | 150
182 | Palo Pinto | 249 | 249 | 150
183 | Panola | 249 | 249 | 150
184 | Parker | 50 | 249 | 150
185 | Parmer | 249 | 249 | 150
186 | Pecos | 249 | 249 | 150
187 | Polk | 249 | 249 | 150
188 | Potter | 249 | 249 | 150
189 | Presidio | 249 | 249 | 150
190 | Rains | 249 | 249 | 150
191 | Randall | 249 | 249 | 150
192 | Reagan | 249 | 249 | 150
193 | Real | 249 | 249 | 150
194 | Red River | 249 | 249 | 150
195 | Reeves | 249 | 249 | 150
196 | Refugio | 249 | 249 | 150
197 | Roberts | 249 | 249 | 150
198 | Robertson | 249 | 249 | 150
199 | Rockwall | 50 | 249 | 150
200 | Runnels | 249 | 249 | 150
201 | Rusk | 249 | 249 | 150
202 | Sabine | 249 | 249 | 150
203 | San Augustine | 249 | 249 | 150
204 | San Jacinto | 249 | 249 | 150
205 | San Patricio | 249 | 249 | 150
206 | San Saba | 249 | 249 | 150
207 | Schleicher | 249 | 249 | 150
208 | Scurry | 249 | 249 | 150
209 | Shackelford | 249 | 249 | 150
210 | Shelby | 249 | 249 | 150
211 | Sherman | 249 | 249 | 150
212 | Smith | 249 | 249 | 150
213 | Somervell | 249 | 249 | 150
214 | Starr | 249 | 249 | 150
215 | Stephens | 249 | 249 | 150
216 | Sterling | 249 | 249 | 150
217 | Stonewall | 249 | 249 | 150
218 | Sutton | 249 | 249 | 150
219 | Swisher | 249 | 249 | 150
220 | Tarrant | 50 | 249 | 150
221 | Taylor | 249 | 249 | 150
222 | Terrell | 249 | 249 | 150
223 | Terry | 249 | 249 | 150
224 | Throckmorton | 249 | 249 | 150
225 | Titus | 249 | 249 | 150
226 | Tom Green | 249 | 249 | 150
227 | Travis | 249 | 249 | 150
228 | Trinity | 249 | 249 | 150
229 | Tyler | 249 | 249 | 150
230 | Upshur | 249 | 249 | 150
231 | Upton | 249 | 249 | 150
232 | Uvalde | 249 | 249 | 150
233 | Val Verde | 249 | 249 | 150
234 | Van Zandt | 249 | 249 | 150
235 | Victoria | 249 | 249 | 150
236 | Walker | 249 | 249 | 150
237 | Waller | 50 | 249 | 150
238 | Ward | 249 | 249 | 150
239 | Washington | 249 | 249 | 150
240 | Webb | 249 | 249 | 150
241 | Wharton | 249 | 249 | 150
242 | Wheeler | 249 | 249 | 150
243 | Wichita | 249 | 249 | 150
244 | Wilbarger | 249 | 249 | 150
245 | Willacy | 249 | 249 | 150
246 | Williamson | 249 | 249 | 150
247 | Wilson | 249 | 249 | 150
248 | Winkler | 249 | 249 | 150
249 | Wise | 50 | 249 | 150
250 | Wood | 249 | 249 | 150
251 | Yoakum | 249 | 249 | 150
252 | Young | 249 | 249 | 150
253 | Zapata | 249 | 249 | 150
254 | Zavala | 249 | 249 | 150