## Issued Turbine Air Permits
TCEQ: Issued Air Permits for Gas Turbines with Electric Output Rated 20 MW or Greater
Version 2023.07.01
This is a list of natural gas-fired turbine projects authorized by TCEQ that generate 20 megawatts (MW) or more greater electric output. It shows their permit numbers, turbine models, number of turbines, power output per turbine and site wide in MW, emissions controls, mode of operation (simple cycle [SC], combined cycle [CC], or cogeneration), and BACT emission concentrations for NOx and CO.
Disclaimer: Blank cells are intentionally blank because there is either no additional permit type associated with the NSR permit, or the information for that field is unavailable.
Permit No. | PSD | NA/S/HAP | Received | Issue Date | Company Name | City | County | Turbine Model | Number of CTs | MW per CT | Project MW | NOx (1) | Control Method | CO (1) | SC/CC | GHG Permit No. | GHG Permit Issue Date
166032 | 1598 |  | 2021-07-29 | 2023-03-13 | Entergy Texas Inc | Orange | Orange | Mitsubishi M501JAC | 2 | 427.9 | 1215 | 2 | DLN+SCR+CO | 2 | CC | GHGPSDTX210 | Pending
168124 |  | S | 2022-02-28 | 2022-03-30 | WATTBRIDGE TEXAS LLC | Huffman | Harris | GE LM6000 | 6 | 50 | 300 | 4 | SCR+CO | 9 | SC | NA
168123 |  | S | 2022-02-28 | 2022-03-16 | WATTBRIDGE TEXAS LLC | Barret | Harris | GE LM6000 | 6 | 50 | 300 | 4 | SCR+CO | 9 | SC | NA
164137 | 1594 | HAP79 | 2021-02-12 | 2021-11-17 | Nacero TX 1 LLC | Penwell | Ector | GE LM2500+G4 | 1 | 35 | 35 | 9 | SCR+CO | 9 | SC | GHGPSDTX207 | 2021-11-17
167417 |  | S | 2021-12-15 | 2022-01-11 | Wattbridge Texas LLC | Angleton | Brazoria | GE LM6000 | 4 | 50 | 200 | 4 | SCR+CO | 9 | SC | NA | NA
167033 |  | S | 2021-11-05 | 2021-11-22 | Remy Jade Generating LLC | Barret | Harris | GE LM6000 | 6 | 50 | 300 | 4 | SCR+CO | 9 | SC | NA | NA
167032 |  | S | 2021-11-05 | 2021-12-20 | WattBridge Energy, LLC | Huffman | Harris | GE LM6000 | 6 | 50 | 300 | 4 | SCR+CO | 9 | SC | NA | NA
166899 |  | S | 2021-10-25 | 2021-11-19 | Wattbridge Texas LLC | Rosharon | Brazoria | GE LM6000 | 2 | 50 | 100 | 4 | SCR+CO | 9 | SC | NA | NA
166721 |  | S | 2021-10-08 | 2021-10-29 | Sky Global Power Two LLC | Sealy | Austin | Siemens SGT-A65 | 4 | 66 | 264 | 4 | SCR+CO | 8 | SC | NA | NA
157526 |  | S | 2019-07-05 | 2019-07-30 | Avocet Power Center | Lufkin | Angelina | GE LM6000 | 3 | 50 | 150 | 4.4 | SCR | 26.3 | SC | NA | NA
157171 |  | S | 2019-06-04 | 2019-06-13 | Goodalta Power Center LLC | Kerens | Navarro | GE LM6000 | 3 | 50 | 150 | 4.4 | SCR | 26.3 | SC
105567 |  | S | eso 02/14/14 8/24/2012 | eso 03/28/14 9/28/2012 | Sargas Texas LLC (prev. Texas En Dev) | Point Comfort | Calhoun | GE LMS100 | 1 | 116 | 250 | 3.4 | DLN+SCR |  | CC | no no. | not @TCEQ
165697 |  | No data | 2021-06-28 | 2021-09-10 | Air Products LLC | La Porte | Harris | GE F6B (Pkg) | 4 | 44 | 176 | 15 | DLN | 15 | COG
38191 | 906M1 | S 165810 S 160357 S 163856 | renew 05/30/2018 02/03/2022 03/03/2020 01/19/2021 | renew 05/30/2018 02/22/2022 03/18/2020 02/05/2021 | Midlothian Energy LLC | Midlothian | Ellis | Alstom GT 24 | 2 4 | 250 275 | 550 1080 | 5 | DLN + SCR | 25 | CC
42734 |  | S 159565 | 6/9/2021 11/4/1999 | 7/2/2021 7/14/2000 | Wise County Power Co LLC (Upgrade to turbines) | Bridgeport | Wise | W 501G | 2 | 230 | 560 | 5 | SCR+CO |  | CC
42179 | 955M1 | S 164774 S 156050 N021M1 | 4/12/2021 3/20/2019 11/3/2011 8/26/1999 | 4/28/2021 4/25/2019 10/15/2012 3/22/2000 | Channel Energy Center, LLC - upgrade to 1 turbine | Pasadena | Harris | Siemens 501F | 1 2 | 180 | No change with this project 740 | 2 3.5 | DLN+SCR | 8 25/15 | CC/COG | 955M1 | 2012-11-29
160538 | 1582 |  | 2020-03-18 | 2021-03-17 | NRG Cedar Bayou 5 LLC | Baytown | Chambers | Mitsubishi MHI501JAC | 1 | 689 | 689 | 2 | DLN + SCR + CO | 4 | SC/CC | 204 | 2021-03-17
163849 |  | S | 2021-01-19 | 2021-01-28 | Brotman Generating LLC | Rosharon | Brazoria | GE LM6000 | 6 | 50 | 300 | 4 | SCR +CO+W | 9 | SC | NA | NA
41996 | 953 | S 163545 N020 | 12/15/2020 8/2/1999 | 1/6/2021 2/11/2000 | Baytown Energy Center LLC - upgrade to 1 turbine | Baytown | Chambers | Westinghouse 501F | 3 | 180 | 750 | 3.5 | D + SCR | 15 | CC/COG
163309 |  | S | 2020-11-16 | 2020-12-16 | Mark One Generating LLC | Angleton | Brazoria | GE LM6000 | 10 | 50 | 500 | 4 | SCR +CO+W | 9 | SC | NA | NA
162101 (prev. authorized under 36889) |  |  | 2020-07-30 | 2020-11-23 | Colorado Bend I Power LLC | Wharton | Wharton | GE Frame 6B (Pkg) | 2 | 46 | 92 | 9 | DLN | 25 | SC | NA | NA
40040 | 923 | S 163072 S 155237 | 10/22/20 01/18/19 12/2/1998 | 11/5/2020 02/06/19 6/8/1999 | Hays Energy LLC | San Marcos | Hays | Alstom GT24 | 4 | Units 2 and 3 upgraded to 293. 175 originally represented | 586 1080 | 5 | SCR, LPM, W, S | 5 (29) | CC
155895 |  | S | 10/20/20 3/7/2019 | 11/4/2020 3/18/2019 | SJRR Power LLC | Houston | Harris | GE LM6000-PD | 2 | 50 | 100 | 4.4 | SCR | 27.3 | SC | NA | NA
153484 |  | S | 9/24/20 9/7/2018 | 10/27/20 9/17/2018 | HO Clarke Generating LLC | Houston | Harris | GE LM6000 PC | 8 | 50 | 100 for this project. 240 originally | 4 | SCR + CO + W | 2 | SC | NA | NA
155736 |  | S | 9/24/20 2/25/2019 | 10/16/20 3/11/2019 | Topaz Generatating LLC | Texas City | Galveston | GE LM6000 | 10 | 50 | 500 | 4 | SCR +CO+W | 9 | SC | NA | NA
162419 |  | S | 2020-08-19 | 2020-09-29 | Sibyl Generating LLC | Houston | Fort Bend | GE LM6000 | 6 | 50 | 300 | 4 | SCR + CO | 9 | SC | NA | NA
110423 | 1366M1 |  | 1/22/20 5/13/13 | 8/17/20 8/1/14 | Ector County Energy Ctr | Goldsmith | Ector | GE 7FA.03 | 2 | 165 | 330 | 9 | DLN | 9 | SC | 49M1 1366GHG | 8/17/20 8/1/14
133367 |  | S | 6/22/2020 6/15/2015 | 7/31/2020 7/3/2015 | Port Comfort Power, LLC | Point Comfort | Calhoun | GE LM6000 (pkg) | 2 | 50 | 100 | 4 | DLN+SCR+CO | 20 | SC | NA | NA
40620 | 931M1 |  | 6/16/20 2/11/1999 | 7/8/20 12/20/1999 | Calpine Bosque Energy Ctr | Whitney | Bosque | GE 7241FA | 3 | 170 | 650 | 9 | D | 9 15 | SC CC | No data | No data
45642 | 979M2 | N036M2 S 96940 S 159448 | 12/13/2019 9/1/2011 | 1/14/2020 9/26/2012 | Calpine - Deer Park Energy Center LLC | Deer Park | Harris | Westinghouse 501F (unit 1-4), Siemens FD2 (unit 5) | 5 | 199 for this project, 180 originally | 199 for this project, 919 total for site | 2.5 (unit 1-4), 2 (unit 5) | DLN+SCR | 8, 4 (unit 5) | CC/COG | 979M2 | 2012-11-29
155311 |  | S | esoc 09/10/20 1/24/2019 | esoc 10/01/20 3/17/2019 | NGO Industrial Holdings LLC | Sealy | Austin | GE LM6000 (pkg) | 4 | 50 | 200 | 4.4 | SCR | 21.9 | SC | NA | NA
155312 |  | S | esoc 09/11/20 1/24/2019 | esoc 10/01/20 3/13/2019 | NGO Industrial Holdings LLC | Palestine | Anderson | GE LM6000 | 4 | 50 | 200 | 4.4 | SCR | 21.9 | SC | NA | NA
154317 |  | S | 2018-11-07 | 2018-12-20 | TX LFG Energy, LP | Alvin | Galveston | GE7FA.04 | 4 | 154 | 154 | 5 | DLN + SCR | 20 | SC | NA | NA
154703 |  | S | 2018-12-06 | 2018-12-20 | ProEnergy Services LLC | Texas City | Galveston | GE LM6000 | 8 | 50 | 400 | 4 | SCR +CO+W | 9 | SC | NA | NA
154565 |  | S | 2018-11-28 | 2018-12-19 | ProEnergy Services LLC | Santa Fe | Gavleston | GE LM6000 | 6 | 50 | 300 | 4 | SCR +CO+W | 9 | SC | NA | NA
154626 |  | S | 2018-11-30 | 2018-12-12 | ProEnergy Services LLC | Iowa Colony | Brazoria | GE LM6000 | 4 | 50 | 200 | 4 | SCR +CO+W | 9 | SC | NA | NA
154465 |  | S | 2018-11-16 | 2018-12-04 | ProEnergy Services LLC | Thompsons | Fort Bend | GE LM6000 | 8 | 50 | 400 | 4 | SCR +CO+W | 9 | SC | NA | NA
152884 |  | S | 2018-07-26 | 2018-08-24 | QEP Energy Company | Tarzan | Martin | GE LM6000 | 2 | 184 | 400 | 4 | SCR | 8 | SC | N/A | N/A
152697 |  | S | 2018-07-11 | 2018-08-10 | Castleman Power Development LLC | Victoria | Victoria | GE LM6000 | 2 | 50 | 100 | 4.4 | SCR | 21.9 | SC | NA | NA
152680 |  | S | 2018-07-10 | 2018-08-10 | Tejas Power Generation LLC | Houston | Harris | Siemens W501D | 1 | 129 | 129 | 3.4 | DLN+ SCR + W | 25 | SC | NA | NA
143912 | 1510 | N256 | 2016-11-14 | 2018-03-27 | Entergy Texas Inc | Willis | Montgomery | Mitsubishi M501GAC | 2 | 368 | 993 - CC | 2 | DLN + SCR + CO | 2 | CC | 163 | 3/27/2018†
121917 | 1422 |  | 2014-07-14 | 2018-02-02 | Southern Pwr Co (Jackson Gen Fac) | Ganado | Jackson | Siemens F(5) | 4 | 230 | 920 | 9 | DLN | 9 | SC | 118 | 6/30/2017†
72579 | 1080 |  | 2015-12-22 | 8/16/2017 4/11/2012 | Golden Spread El. Coop Mustang | Denver City | Yoakum | GE F7FA | 1 | 168 | 168 | 9 | DLN | 9 | SC | 138 | 2017-08-16
146805 |  | S | 2017-05-12 | 2017-06-15 | Victoria Port Power LLC | Victoria | Victoria | GE LM6000 | 2 | 50 | 100 | 4 | DLN + SCR | 20 | SC
146823 |  | S | 2017-05-12 | 2017-06-09 | Victoria City Power LLC | Victoria | Victoria | GE LM6000 | 2 | 50 | 100 | 4 | DLN + SCR | 20 | SC
135322 | 1470 |  | 2015-08-24 | 2017-04-28 | Southwestern Public Svc Co (Xcel Energy) | Seminole | Gaines | SGT6-5000F5 | 4 | 227 -SC 426 - CC | 910 - SC 1706 - CC | 9 -15 SC 2 - CC | DLN - SC DLN+SCR+CO - CC | 9 -20 SC 2 CC | SC/CC | 141 | 2017-04-28
140763 | 1500 |  | 5/18/2016 12/21/2012 | 4/17/2017 8/8/2014 | Formosa Plastics Corporation, Texas (Split CTs 7 & 8 from Pmt 19166 onto own permit) | Point Comfort | Calhoun | SGT6-2000E | 2 | 117 | 234 | 2 | DLN + SCR + CO | 4 | CC/COG
131316 | 1454 |  | 2016-10-10 | 2017-02-14 | FGE Eagle Pines, LLC (Different turbines, Alstoms no longer available) | New Summerfield | Cherokee | GE 7HA / Siemens 5000F | 6 / 9 | 346 / 242 | 3408 | 2 | DLN + SCR + CO | 2 | CC | 133* | 2015-11-04
123117 | 1460 | N204 | 2014-08-29 | 2017-02-10 | INEOS USA (Chocolate Bayou, NRG Tx Pwr LLC) | Alvin | Brazoria | GE LM6000 | 2 | 50 | 100 | 2.5 | DLN + SCR + CO | 4 | CC/COG | 135 | 2017-02-10
110025 | 1364 |  | 2016-08-08 | 2016-12-16 | FGE Texas (FGE Power, Different Turbines) | Westbrook | Mitchell | SGT6-5000F | 4 CTs Iss. 3/14 | 242 | 1448 | 2 | DLN + SCR + CO | 2 | CC | 36 | 2016-12-12
130051 | 1450 |  | 2015-02-09 | 2016-04-07 | Brazos Electric | Grandview | Hill | GE FA.03, 04, or 05 or SGT6F5ee | 4 | 154 - 232 | 616 - 928 | 9 | DLN | 9 | SC | 131 | 2016-04-07
107569 | 1432 |  | 2014-08-19 | 2016-03-08 | DeCordova II Pwr Co LLC (Luminant) | Granbury | Hood | Add stm turb | CTs Iss. 8/29/13 |  | 310-350 | - | - | - | CC | 124 | 2016-10-03
138452 |  | S | 2016-01-27 | 2016-03-04 | Castleman Pwr Systems Int'l LLC | Houston | Harris | GE LM6000 | 2 | 50 | 100 | 4 | DLN + SCR | 20 | SC
120973 | 1420 |  | 2014-06-23 | 2015-12-09 | Navasota South Peakers Op Co LLC | Nixon | Wilson | GE 7FA.04 | 3 | 183 | 550 | 9 | DLN | 9 | SC | 117 | 2015-12-16
135738 |  | S | 2015-09-15 | 2015-11-06 | Powersite LLC | Wink | Winkler | R-R Trent 60 | 4 | 58 | 372 | 2.5 | DLN + SCR | 3 | CC
132827 |  |  | 2015-05-26 | 2015-11-05 | NTE Texas LLC (rev. 117537) | Blackwell | Nolan | GE FA.04 | 2 | 184 | 328 | 9 | DLN | 9 | SC
131316 | 1454 |  | 2015-03-27 | 2015-11-04 | FGE Eagle Pines, LLC | New Summerfield | Cherokee | Alstom GT36 | 6 | 318 | 3408 | 2 | DLN + SCR + CO | 2 | CC | 133* | 2015-11-04
121051 | 1418 |  | 2014-06-23 | 2015-10-27 | Navasota North Peakers Op Co LLC | Van Alstyne | Grayson | GE 7FA.04 | 3 | 183 | 550 | 9 | DLN | 9 | SC | 119 | 2016-01-13
130017 |  |  | 2015-02-09 | 2015-10-15 | Luminant Gen Co LLC - Permian Basin Sta. | Monahans | Ward | GE FA.05 or S F5ee | 2 | 210 or 231 | 420 or 632 | 9 | DLN | 7.5 4 | SC
77679 | 1061M1 |  | 2014-01-15 | 2015-10-14 | Nacogdoches Pwr LLC (Southern Co.) | Cushing | Nacogdoches | Siemens F5 | 1 | 232 | 232 | 9 | DLN | 9 | SC | 116 | 2016-03-01
125963 | 1442 |  | 2014-11-25 | 2015-10-09 | Shawnee Energy Center (repermit w/o SCR) | Abbott | Hill | S GT6-5000F | 4 | 230 | 920 | 9 | DLN | 9 | SC | 126 | 2015-11-10
128432 |  |  | 2014-12-23 | 2015-09-10 | Valley NG Pwr Co LLC (Luminant) | Savoy | Fannin | GE FA.05 or S F5ee | 2 | 210 or 231 | 420 or 632 | 9 | DLN | 7.5 4 | SC
117026 | 1390 | N194 | 2014-01-27 | 2015-06-18 | Eagle Mtn Pwr Co LLC (Luminant) | Fort Worth | Tarrant | GE 7FA.05 or S GT6-5000F | 2 | 210 or 231 | 730 or 812 | 2 | DLN + SCR + CO | 2 | CC | 115 | 2016-07-19
109148 | 1358M1 |  | 2014-07-15 | 2015-05-12 | Golden Spread El. Coop. - Antelope Elk Sta. | Abernathy | Hale | GE 7FA.05 | 3 | 202 | 600 | 9 | DLN | 9 | SC | 41M1 | 2015-05-20
120849 | 1414 |  | 2014-06-18 | 2015-05-08 | Navasota South Peakers Op Co LLC | Seguin | Guadalupe | GE 7FA.04 | 3 | 183 | 550 | 9 | DLN | 9 | SC | 120 | 2015-11-10
131873 |  | S | 2015-04-15 | 2015-05-08 | Net Power, LLC (demo project) | LaPorte | Harris | Toshiba CO2 | 1 | 25 | 25 | * | oxyfired | * | CO2
118549 |  |  | 2014-03-28 | 2015-05-05 | Wharton County Gen LLC (GDF Suez NA) | Boling | Wharton | GE 7FA.05 | 1 | 230 | 230 | 9 | DLN | 9 | SC
119365 | 1410 |  | 2014-04-18 | 2015-04-01 | Colorado Bend II Power LLC | Wharton | Wharton | GE 7HA.02 | 2 | 330 | 1160 | 2 | DLN + SCR + CO | 4 | CC | 112 | 2015-04-01
48106 | 1012M2 |  | 9/13/2013 11/29/2007 5/30/2001 | 3/20/2015 9/24/2008 4/12/2002 | City of Austin - Sand Hill Energy Center | Del Valle | Travis | GE 7FA.04 GE LM6000 GE LM6000 GE F7FA | 1 2 4 1 | 173.9 48 48 164 | 173.9 96 500 | 2 5 5 5 | DLN+SCR+CO DLN+SCR DLN+SCR | 2 9 9 17.5 | CC SC SC CC | 1012M2GHG | 2014-09-29
122003 | 1424 |  | 2014-07-18 | 2015-02-09 | Rockwood Energy Center LLC | Garwood | Colorado | GE F.05 or H.01 MHI 501GAC,or S SCC6-8000F | 2 | 234 - 343 | 748 - 915 | 2 | DLN + SCR + CO | 2 | CC | 122 | 2016-03-18
111724 | 1374 |  | 2013-06-18 | 2015-02-02 | Indeck Wharton, LLC | Danevang | Wharton | GE 7FA or Siemens 5000F | 3 | 220 | 650 | 9 | DLN | 9 | SC | 1374GHG | 2014-05-12
117537 |  |  | 2014-02-13 | 2014-12-19 | NTE Texas LLC | Blackwell | Nolan | MHI 501GAC | 1 | 273 | 273 | 9 | DLN | 9 | SC
124811 |  | S | 2014-10-29 | 2014-12-03 | Shawnee Energy Center | Abbott | Hill | S GT6-5000F | 4 | 230 | 920 | 4 | DLN + SCR | 2 | SC
108819 | 1354 |  | 2013-02-22 | 2014-12-02 | M & G Resins USA, LLC | Corpus Christi | Nueces | GE LM6000 | 1 | 38 | 38 | 2 | DLN+SCR+CO | 2 | CC | 1354GHG | 2014-11-18
108258 | 1348 |  | 2013-02-14 | 2014-12-01 | Victoria WLE LP | Victoria | Victoria | GE 7FA.04 or equivalent | 1 | 275 | 450-460 | 2 | DLN+SCR+CO | 2 | CC | 1348GHG | 2014-10-08
111393 | 1368 |  | 2013-06-27 | 2014-11-20 | Southern Power Company | Trinidad | Henderson | Mitsubishi J model | 1 | 450 | 530 | 2 | DLN+SCR+CO | 4 | CC | 125 | 2016-03-01
122777 |  | S | 2014-08-18 | 2014-09-17 | Powersite LLC | Perrin | Jack | R-R Trent 60 DLE ISI | 4 | 60.55 | 372 | 3 | DLN+SCR+CO | 3 | CC
19166 | 760M9 | HAP10 | 4/20/2000 11/7/1988 | 5/3/2001 10/13/1989 | Formosa Plastics Corporation, Texas | Point Comfort | Calhoun | GE F7EA (CT 6) GE F7EA (CTs 1-5) | 1 5 | 83 88 | 80 475 | 9 25 | DLN S | 25 | CC/COG | 1389GHG | 2014-08-01
104840 | 1302 |  | 2012-07-20 | 2014-07-16 | Freeport LNG Development, LP | Quintana | Brazoria | GE F7E | 1 | 87 | 87 | 2 | DLN+SCR+CO | 4 | CC
120681 |  | S | 2014-06-11 | 2014-07-15 | Optim En. Twin Oaks (repowering) | Bremond | Robertson | GE 7FA.05 or S GT-5000F | 2 | 225 or 230 | 668 | 5 | DLN+SCR+CO | 5 | CC
108182 |  |  | 2013-02-06 | 2014-05-20 | NRG Tx Pwr LLC (PH Robinson Sta) | Bacliff | Galveston | GE F7E | 6 | 65 | 390 | 15 | DLN | 25 | SC
109148 | 1358 |  | 2013-04-01 | 2014-04-22 | Golden Spread El. Coop. - Antelope Elk Sta. | Abernathy | Hale | GE 7FA.05 | 1 | 190 | 190 | 9 | DLN | 9 | SC | 1358GHG | 2014-06-02
118876 |  | S | 2014-04-07 | 2014-04-11 | Apex Bethel En Ctr LLC (reissue) | Tenn. Colony | Anderson | D-R EA-418 (CAES) | 2 | 158 | 317 | 2.5 | W+SCR+CO | 5 | CAES | 104511GHG | 2014-03-13
110025 | 1364 |  | 2013-05-06 | 2014-03-24 | FGE Power, LLC | Westbrook | Mitchell | Alstom GT24 | 4 | 231 | 1600 | 2 | DLN+SCR+CO | 2 | CC | 1364GHG | 2014-04-28
110357 |  |  | 2013-05-23 | 2014-02-07 | Tradinghouse Pwr Co LLC (Luminant) | Waco | McLennan | GE 7FA.05 or S GT6-5000F(5) | 2 | 225-230 | 450-460 | 9 | DLN | 9 | SC
115851 |  | S | 2013-12-13 | 2014-01-27 | Powersite LLC | Kenedy | Karnes | R-R Trent 60 DLE ISI | 4 | 60.55 | 372 | 3 | DLN+SCR+CO | 3 | CC
103839 | 1298 |  | 2012-06-22 | 2013-11-12 | Pinecrest Energy Center LLC | Lufkin | Angelina | GE 7FA.05 or S GT6-5000F | 2 | 183-225 | 637-721 | 2 | DLN+SCR+CO | 2 | CC | 1298GHG | 2014-07-31
107569 |  |  | 2012-12-27 | 2013-08-29 | DeCordova II Pwr Co LLC (Luminant) | Granbury | Hood | GE 7FA.05 or S GT6-5000F(5) | 2 | 225-230 | 450-460 | 9 | DLN | 9 | SC
108130 |  | S | renew 01/12/22 2/5/2013 | renew 01/12/22 2/27/2013 | Chamisa CAES at Tulia LLC | Tulia | Swisher | D-R (CAES) | 2 | 135 | 270 |  | SCR+CO |  | CAES | 108130 | 2014-03-21
101542 | 1288 |  | 2012-03-15 | 2013-02-07 | La Paloma Energy Center | Harlingen | Cameron | GE 7FA.04 or SGT6-5000F | 2 | 183-232 | 637-735 | 2 | DLN+SCR+CO | 2 | CC | 1288GHG | 2013-11-16
98664 | 1268 | N138 | 2011-09-19 | 2012-12-21 | Petra Nova Parish Holdings (aka NRG Tx, WA Parish CO2 proj) | Thompson | Fort Bend | GE F7EA | 1 | 80 | 80 | 2 | DLN+SCR | 9 | SC/COG
103230 |  | S | 2012-05-29 | 2012-06-27 | Friendswood En. Genco LLC | Houston | Harris | W 501D5 | 1 | 128 | 128 | 3.4 | DLN+SCR | 9 | SC
98073 |  |  | 2011-08-15 | 2012-04-30 | Xcel/SWPSC Jones 4 | Lubbock | Lubbock | S GT6-5000F | 1 | 175 | 175 | 9 | DLN | 9 | SC
93938 | 1244 |  | 2010-10-29 | 2011-09-01 | LCRA - TC Ferguson Pwr Plant | Horseshoe Bay | Llano | GE F7FA | 2 | 175 | 550 | 2 | DLN+SCR+CO | 4 | CC | 1244GHG | 2011-11-10
92156 |  |  | 2010-03-26 | 2010-11-01 | Xcel/SWPSC Jones 3 | Lubbock | Lubbock | S GT6-5000F | 1 | 175 | 175 | 9 | DLN | 9 | SC |  | No information, end of column move to A90
87153 | 877 |  | 2009-01-02 | 2010-03-15 | Gregory Power (repermit/renew) | Gregory | San Patricio | GE F7FA | 2 | 168 | 336 | 9 | DLN | 20 | SC
83638 | 1110 |  | 2007-12-07 | 2010-03-03 | Wolf Hollow II Pwr LLC (Exelon) | Granbury | Hood | GE 7HA.02 | 2 | 330 | 1160 | 2 | DLN + SCR + CO | 4 | CC
87225 | 1198 |  | 2008-12-22 | 2010-02-03 | Panda Sherman Power LLC | Sherman | Grayson | S GT6-5000F | 2 | 200 | 600 | 2/9 | DLN+SCR | 4/15 | CC
83801 | 1117 |  | 2008-01-04 | 2008-11-17 | Brazos Electric Power Coop Inc | Bridgeport | Jack | GE F7FA | 2 | 172 | 663 | 2 | DLN+SCR | 11 | CC
83503 | 1111 |  | 2007-12-03 | 2008-10-10 | Panda Temple Power LLC | Temple | Bell | S GT6-5000F | 4 | 200 | 1000 | 2 | DLN+SCR | 9 | CC
81903 | 1095 |  | 2007-05-14 | 2008-09-05 | City Public Service | Elmendorf | Bexar | GE LM6000 | 4 | 50 | 200 | 5 | DLN+SCR+CO | 9 | SC
46189 | 1103 | N71 | renew 06/03/21 10/4/2007 | renew 02/22/2022 7/29/2008 | Texas Medical Center (prev. Thermal Energy) | Houston | Harris | GE LM6000 | 1 | 50 | 100 | 2 | DLN+SCR | 29 | SC
83550 |  |  | 2007-12-06 | 2008-07-24 | East TX Electric Coop Inc | Kountze | Hardin | GE F7EA | 2 | 73 | 146 | 9 | DLN | 25 | SC
4415 |  |  | 2008-03-07 | 2008-06-30 | City of Bryan - Dansby Power Plant | Bryan | Brazos | GE LM6000 | 1 | 50 | 50 | 5 | W+SCR+CO | 9 | SC
83551 |  |  | 2007-12-06 | 2008-06-26 | East TX Electric Coop Inc | Shepherd | San Jacinto | GE F7EA | 2 | 73 | 146 | 9 | DLN | 25 | SC
1467 | 1090 | N 284 S 114528 | 11/16/19 10/22/13 4/4/2007 | 08/27/21 01/17/14 5/22/2008 | El Paso Electric Co | El Paso | El Paso | Mitsubishi 501G GE F7EA W501-B6 | 1 (new) 4 | 230 (new) 69 | 288 | 2.5 (new) 3 42 | DLN+SCR+CO W | 3 (new) 25 -- | SC/CC | 199
83475 |  | S | 4/26/2021 11/28/2007 | 5/13/2021 12/28/2007 | Lower Colorado River Authority | Winchester | Fayette | GE LM6000 (Pkg) | 4 | 50 | 200 | 5 | DLN+SCR | 25 | SC
81593 | 1093 |  | 4/10/2007 7/72020 | 12/18/2007 5/7/2021 | Barney M. Davis LP | Corpus Christi | Nueces | GE F7FA | 2 | 172 | 700 | 9 SC 5 CC | DLN+SCR+CO | 8 SC 5 CC | SC/CC
81594 | 1091 |  | 4/10/2007 12/16/2020 | 12/18/2007 7/6/2021 | Nueces Bay WLE LP | Corpus Christi | Nueces | GE F7FA | 2 | 172 | 700 | 9 SC 5 CC | DLN+SCR | 8 SC 5 CC | SC/CC
82519 |  | S | 2007-07-30 | 2007-08-17 | Laredo WLE, LP | Laredo | Webb | GE LMS1000 | 2 | 100 | 200 | 5 | DLN+SCR | 9 | SC
80289 | 1082 |  | 2006-10-31 | 2007-07-26 | NRG Texas - Cedar Bayou Unit 4 | Eldon | Chambers | S GT6-5000F | 2 | 200 | 600 | 3 | DLN + SCR | 15 | CC
80878 |  | S | 2007-01-11 | 2007-02-02 | Nucoastal Energy | Victoria | Victoria | MHI M501F | 1 | 285 | 323 | 5 | DLN+SCR | 19 | CC
76990 | 1059 |  | 2005-09-26 | 2006-02-14 | Navasota Odessa Energy Partners LP | Odessa | Ector | GE F7EA | 4 | 75 | 550 | 5 | DLN+SCR | 27 | CC
77039 | 1060 |  | 2005-10-03 | 2006-02-09 | Colorado Bend I Power LLC | Wharton | Wharton | GE F7EA | 4 | 75 | 550 | 5 | DLN+SCR | 31 | CC
72579 |  |  | 2004-07-02 | 2005-01-10 | Golden Spread El. Coop Mustang Unit 4 | Denver City | Yoakum | GE F7FA | 1 | 168 | 168 | 9 | DLN | 9 | SC
46306 | 986M1 | N59 | 2004-04-13 | 2004-12-02 | Dow Chemical GT96 (Calpine owner) | Freeport | Brazoria | W 501F | 1 | 180 | 236 | 5/3 | DLN+SCR | 25 | CC
55627 |  | S | 2003-06-26 | 2003-09-08 | Brownsville PUB Silas Ray Unit 10 | Brownsville | Cameron | GE LM6000 | 1 | 50 | 50 | 5 | SCR | 32 | SC
52756 | 1026 |  | 2002-09-25 | 2003-07-23 | Brazos Elec Pwr (Duke Energy) | Jacksboro | Jack | GE F7FA | 2 | 170 | 620 | 5 | SCR | 20 | CC
53284 | 1027 |  | 2002-10-15 | 2003-06-27 | City Public Service Leon Creek | San Antonio | Bexar | GE LM6000 | 4 | 48 | 180 | 5 | SCR+CO | 12 | SC
54162 |  | S | 2003-02-04 | 2003-03-28 | City of Bryan - Dansby Power Plant | Bryan | Brazos | GE LM6000PC | 1 | 50 | 50 | 5 | SCR | 32 | SC
7647B | 276 |  | 2000-11-10 | 2002-12-20 | OxyVinyls, LP - Unit 3 | La Porte | Harris | GE F7EA | 1 | 87 | 87 | 4 | DLN+SCR | 25 | COG
48070 | 1011 |  | 2001-05-24 | 2002-01-17 | South Texas Electric Coop, Inc | Nursery | Victoria | GE LM6000 | 3 | 45 | 180 | 5 | SCR | 15 | CC
45642 | 979 | N036 | 2000-09-05 | 2001-08-22 | Calpine - Deer Park Energy Ctr | Deer Park | Harris | W 501F | 4 | 180 | 1060 | 2.5 | SCR | 24 | CC
46042 | 981 |  | 2000-10-16 | 2001-07-12 | BP Amoco Corp | Texas City | Galveston | GE F7FA | 3 | 167 | 550 | 3.5 | SCR | 25 | CC
45360 | 977 |  | 2000-08-16 | 2001-05-23 | Entergy Power Ventures LP | Marshall | Harrison | GE F7FA | 2 | 170 | 570 | 5 | SCR | 25 | CC
21878 |  |  | 2000-08-30 | 2000-12-19 | Air Products, Inc. | La Porte | Harris | GE F6B (Pkg) | 4 | 44 | 176 | 15 | DLN | 15 | COG
43890 | 965 |  | 2000-03-20 | 2000-12-15 | Cottonwood Energy Co. LP | Deweyville | Newton | GE F7FA | 4 | 170 | 1200 | 5 | SCR | 17.6 | CC
43965 | 966 | N026 | 2000-03-24 | 2000-10-17 | Calpine - Brazos Valley (Avista-Steag) | Thompsons | Fort Bend | GE F7FA | 2 | 175 | 670 | 3.5 | SCR | 25 | CC
41249 | 940 |  | 1999-04-30 | 2000-03-28 | Calpine - Freestone Energy Center | Fairfield | Freestone | GE F7FA | 4 | 175 | 1070 | 9 | D | 20 | CC
41941 | 948 |  | 1999-07-28 | 2000-03-22 | Coastal Power Company | Bastrop | Bastrop | GE F7FA | 2 | 170 | 550 | 9 | D | 20 | CC
41953 | 951 |  | 1999-07-29 | 2000-03-06 | Next Era - Forney Plt (Cobisa-Forney) | Forney | Kaufman | GE F7FA | 6 | 170 | 1774 | 9 | D | 15 | CC
40803 | 935 |  | 1999-03-09 | 2000-02-23 | City of Garland | Nevada | Collin | GE F7EA | 1 | 85 | 85 | 9 | D | 25 | SC
41166 | 939 |  | 1999-04-22 | 2000-02-07 | Exelon Wolf Hollow 1 (AES Aurora) | Granbury | Hood | M 501G | 2 | 254 | 807 | 9 | SCR | 25 | CC
41500 | 943 |  | 1999-05-28 | 2000-02-04 | Calpine - Corpus Christi En Ctr | Corpus Christi | Nueces | GE F7FA | 2 | 166 | 500 | 9 | D | 15 | CC
40363 | 927 |  | 1999-01-21 | 1999-12-15 | Ennis-Tractebel Power Co., Inc. | Ennis | Ellis | W 501G | 1 | 250 | 350 | 9 | SCR | 20 | CC
41775 | 946 | N017 | 1999-07-06 | 1999-12-09 | Reliant Energy Channelview LP | Channelview | Harris | W 501F | 4 | 183 | 820 | 3 | D + SCR | 23 | CC
40867 | 938 |  | 1999-03-17 | 1999-12-03 | Rio Nogales Power Project LP | Seguin | Guadalupe | GE F7FA | 3 | 170 | 780 | 9 | D | 7.4 | CC
| 906M1 | S 163856 S 160357 | 7/1/1999 4/13/1998 | 11/24/1999 10/2/1998 | Midlothian Energy LLC | Midlothian | Ellis | ABB GT24 OTC | 2 4 | 250 275 | 550 1080 | 5 | SCR | 25 | CC
39842 | 919 |  | 1998-11-12 | 1999-11-19 | Eastman Cogen LP (Eastex Cogen) | Longview | Harrison | GE F7FA | 2 | 168 | 460 | 9 | D | 7 | CC/COG
41008 | 936 |  | 1999-04-05 | 1999-11-19 | Odessa-Ector Pwr Partners LP | Odessa | Ector | GE F7FA | 4 | 170 | 1000 | 9 | D | 9 | CC
38481 | 921 |  | 1998-05-29 | 1999-10-20 | Union Carbide | Seadrift | Calhoun | GE F6B | 1 | 39 | 39 | 9 | D | 25 | COG
41437 | 941 |  | 1999-05-21 | 1999-09-30 | GenTex Power Corp & Calpine | Bastrop | Bastrop | W 501F | 2 | 183 | 500 | 5 | SCR | 10/25 | CC
40496 | 929 |  | 1999-02-01 | 1999-06-22 | SRW Cogen LP (EI DuPont) | Orange | Orange | GE F7FA | 2 | 170 | 440 | 6 | SCR | 15 | CC/COG
40039 | 925 |  | 1998-12-02 | 1999-05-07 | Tenaska Gateway | Minden | Rusk | GE F7FA | 3 | 164 | 888 | 9 | D | 25 | CC
36644 | 903 | N007 | 1998-10-12 | 1999-04-21 | Fina/BASF Amd - Cogen for Blr | Port Arthur | Jefferson | GE F6B | 2 | 39 | 78 | 9 | D/SCR | 25 | COG
38659 | 922 |  | 1998-06-24 | 1999-02-15 | Guadalupe Power Partners | Marion | Guadalupe | GE F7FA | 4 | 170 | 1000 | 9 | D | 15 | CC
37894 | 918 |  | 1998-03-19 | 1999-01-08 | Lubbock Power & Light | Lubbock | Lubbock | GE LM6000PC | 2 | 42 | 128 | 15 | SCR | 25 | CC
38284 | 909 |  | renew 03/06/18 5/1/1998 | renew 06/08/18 12/31/1998 | Calpine - Magic Valley Gen Sta | Edinburg | Hidalgo | W 501G | 2 | 230 | 700 | 12/9 | SCR | 25 | CC
38599 | 914 |  | renew 03/06/18 6/15/1998 | renew 06/04/18 12/22/1998 | Calpine - Hidalgo En Ctr (Duke En) | Edinburg | Hidalgo | GE F7FA | 2 | 175 | 520 | 9/12 | D | 20 | CC
38326 | 916 |  | 8/30/2022 renew 11/27/17 5/7/1998 | 02/24/2023 renew 05/24/19 10/28/1998 | Luminant Generation Company LLC (prev. Nextera) | Paris | Lamar | GE F7FA | 4 | 182 | 1118 | 13 | DLN + CO | 18.4 | CC
38183 | 907 |  | renew 01/04/18 4/20/1998 | renew 03/20/18 10/14/1998 | City Public Service | Elmendorf | Bexar | GE F7FA | 2 | 170 | 500 | 9 | SCR | 25 | CC
31914 | 857 |  | renew 02/26/19 12/10/1997 | renew 05/9/19 9/30/1998 | Sweeny Cogeneration LLC | Old Ocean | Brazoria | W 501D5A | 4 | 121 | 121 | 25/15 | D | 10 | COG
37283 | 915 | N015 | renew 08/14/18 12/18/1997 | renew 02/28/19 9/30/1998 | Pasadena Cogeneration LP | Pasadena | Harris | W 501F | 3 | 160 | 500 | 9/6 12 | SCR | 25 20 | CC/COG
37391 | 897 |  | renew 10/04/17 1/13/1998 | renew 03/19/18 8/7/1998 | Tenaska Frontier Partners | Shiro | Grimes | GE F7FA | 3 | 183 | 830 | 15 | D | 13 | CC
37613 | 900 |  | renew 07/23/19 2/12/1998 | renew 09/27/19 7/31/1998 | Frontera Generating LP | Mission | Hidalgo | GE F7FA | 2 | 165 | 440 | 15 | D | 15 | CC
735B | 908 |  | renew 04/05/13 12/8/1997 | renew 10/31/13 6/26/1998 | BASF - Cogen 15-2-1 | Freeport | Brazoria | GE F7EA | 1 | 83 | 83 | 15 | D | 25 | COG
35335 | 880 |  | renew 09/14/07 4/18/1997 | renew 06/11/18 1/8/1998 | Occidental Chem | Gregory | San Patricio | GE-7231FA | 2 | 166 & 185 | 500 | 15 | D | 20 | CC
32881 | 875 |  | renew 10/31/16 12/31/1996 | renew 07/11/17 7/17/1997 | Golden Spread El. Coop. - Mustang (LS Pwr) | Denver City | Yoakum | GE F7FA | 2 | 180 | 550 | 15 | D | 15 | SC/CC
32096 | 867 |  | renew 01/25/16 3/11/1996 | renew 03/30/17 2/5/1997 | Borger Energy Associates, L.P. (prev. Quixx Corp) | Borger | Hutchison | W 501D5A | 2 | 115 | 242 | 15 | D + SCR | 25 | COG
31914 | 857 |  | renew 02/26/19 2/12/1996 | renew 05/29/19 9/9/1996 | Sweeny Cogen LLC | Old Ocean | Brazoria | W 501D5A | 4 | 121.3 | 363 | 25/15 | D + SCR | 10 | COG
25738 | 840 |  | renew 10/29/14 7/15/1994 | renew 01/23/15 4/21/1995 | Brownsville Public Utility Board | Brownsville | Cameron | W 251B | 1 | 45 | 70 | 15 | D + SCR | 10 | SC/CC
25384 | 839 |  | renew 01/31/14 6/20/1994 | renew 04/0914 12/6/1994 | Brazod Electric Power Coop (orig. Tenaska IV Power) | Cleburne | Johnson | W 501F | 1 | 162 | 500 | 9 | SCR | 25 | CC
9629 |  |  | renew 05/24/13 11/13/1992 | renew 02/18/20 5/12/1994 | The Dow Chemical Company (orig. E. I. DuPont) | Orange | Orange | GE PG711 | 1 | 83 | 105 | 42 | S | 10 | CC/COG
9241A | 493M1 |  | renew 03/09/12 11/5/1992 | renew 04/08/13 11/8/1993 | Optim En. Altura (Cogen Lyondell) CT #6 | Channelview | Harris | GE F7EA | 1 | 80 | 80 | 15 | D | 25 | COG
22038 | 815 |  | renew 04/08/14 11/5/1992 | renew 01/13/15 8/9/1993 | Deer Park Refining, L.P. (orig. Shell Oil Co) | Deer Park | Harris | GE F7E | 2 | 75 | 150 | 15 | D (SCR retro) | 25 | COG
21394 | 806 |  | renew 02/04/13 3/3/1992 | renew 10/21/13 6/16/1993 | Brazos Electric Power Coop | Palo Pinto | Palo Pinto | W 501D5 | 2 | 104 | 208 | 25 | W | 25 | SC
21587 | 807 |  | renew 02/27/13 5/15/1992 | renew 09/23/13 5/27/1993 | NRG San Jac Station (Hou Ind Inc) | LaPorte | Harris | GE F7EA | 2 | 81 | 162 | 15 | DLN | 132 | COG
21592 |  |  | renew 01/29/13 5/14/1992 | renew 10/07/13 11/12/1992 | NRG (Upgrade THWharton 3 + 4) (H Ind Inc) | Satsuma | Harris | GE F7E (Hybrid) | 8 | 70 | 564 | 25 | DLN | 25 | CC
21429 |  |  | renew 10/09/12 3/11/1992 | renew 05/29/13 9/14/1992 | Air Liquide P Neches ASU Cogen (Big Three) | Port Neches | Jefferson | GE F6 | 1 | 37 | 37 | 9 | LPM+SCR | 15 | COG
2894 |  |  | renew 01/02/13 4/24/1992 | renew 07/11/13 7/29/1992 | NRG Texas Power LLC (orig. HL&P) | Houston | Harris | BB 11D5 (Trbdn) | 6 | 72 | 362 | 55 | W |  | SC
20869 | 800 |  | renew 10/18/12 6/3/1991 | renew 09/90/15 5/20/1992 | Freeport Power Limited (Oyster Creek Cogen.) | Freeport | Brazoria | GE F7EA 7111 | 3 | 85 | 435 | 15 | DLN | 25 | CC/COG
19764 |  |  | renew 06/15/15 10/16/1989 | renew 06/26/15 4/6/1990 | Praxair INC (prev. Niject Services) | Hawkins | Wood | GE LM2500 | 1 | 26 | 26 | 25 | S + DLN | 187 | COG
18846 |  |  | renew 05/24/13 5/2/1988 | renew 03/03/14 8/3/1988 | City of Lubbock (Texas Tech Cogen.) | Lubbock | Lubbock | GE LM2500 | 1 | 21 | 21 | 25 | S |  | COG
18358 | 732 |  | renew 01/14/13 9/30/1987 | renew 05/30/13 7/5/1988 | Equistar Chemical, LP | Corpus Christi | Nueces | GE F6 | 1 | 37 | 37 | 42 | S |  | COG
18049 | 725 |  | renew 02/19/13 4/15/1987 | renew 06/14/13 6/14/1988 | Ticona Polymers, Inc (Celanese) | Bishop | Nueces | GE F6 | 1 | 47.4 |  | 42 | S |  | COG
18394 | 739 |  | renew 01/05/11 10/15/1987 | renew 05/22/12 5/19/1988 | Direct En. Paris Gen. (orig. Tenaska) | Paris | Lamar | GE F7EA | 2 | 84 | 244 | 42 | S |  | CC/COG
17411 | 720 |  | renew 12/12/14 7/7/1986 | renew 06/18/15 9/29/1986 | Bher Power Resources, INC. | Big Spring | Howard | GE F7EA | 2 | 90 | 200 | 51 | S |  | CC/COG
16750 | 685 |  | renew 11/07/11 10/17/1985 | renew 06/26/12 6/10/1986 | Signal Hill Wichita Falls Power | Wichita Falls | Wichita | GE LM2500 | 3 | 20 | 77 | 107 | S |  | CC
17030 | 699 |  | renew 09/21/12 2/12/1986 | renew 12/19/12 5/29/1986 | Formosa Plastics | Point Comfort | Calhoun | GE PG6001B (F6) | 1 | 38.7 |  | 94 | S |  | CC/COG
9664 | 662 |  | renew 02/22/2 3/28/1985 | renew 02/22/12 2/12/1986 | Luminant Gerneration Company LLC (prev. TXU) | Granbury | Hood | GE F7EA | 4 | 65 | 260 | 96 | W |  | SC/CC
9560 |  |  | renew 02/10/14 11/26/1984 | renew 02/13/15 2/11/1986 | Invista S.ar.l (orig. E. I. DuPont) | Victoria | Victoria | GE F7 | 1 | 96 |  | 10 (30 day) 30 (24 hr) | S (SCR retro to 10) |  | SC/COG
9668 | 661 |  | renew 04/14/16 3/28/1985 | renew 06/28/16 1/29/1986 | Luminant Generation Company LLC (prev. TXU) | Colorado City | Mitchell | GE 7EA (pkg) | 6 | 65 | 390 | 96 | W |  | SC
9659 | 663 |  | renew 01/26/15 3/28/1985 | renew 04/06/15 1/29/1986 | Luminant Generation Company LLC (prev. TXU) | Monahans | Ward | GE 7EA | 5 | 94 | 325 | 96 | W |  | SC
9629 |  |  | renew 05/24/13 3/6/1985 | renew 02/18/20 9/27/1985 | Performance Materials NA Inc. (prev E. I. Dupont) | Orange | Orange | GE PG711 | 1 | 83 |  | 42 | S | 10 (CT only) 500 (CT + duct) | COG
9609A |  |  | renew 12/18/14 2/5/1985 | renew 05/29/15 8/2/1985 | Union Carbide | Seadrift | Calhoun | GE MS-6001 | 2 | 35 |  | 75 | S |  | COG
9570 | 650 |  | renew 05/08/15 12/10/1984 | renew 05/11/15 6/21/1985 | Calpine - Texas City Cogen LP | Texas City | Galveston | W 501D5 | 3 | 100 | 400 | 75 | S + DLN (units 2 and 3) |  | CC/COG
9463 | 649 |  | units replaced 10/29/18 5/3/1984 | units replaced 01/24/19 4/11/1985 | South Houston Green Power LLC (prev. Amoco) | Texas City | Galveston | GE F7 | 2 | 77 |  | 75 | S + SCR retrofit |  | COG
9322 | 621 |  | renew 05/17/19 4/15/1983 | renew 09/13/19 2/8/1985 | University of Texas | Austin | Travis | W 251 | 1 | 45 |  | 75 | S |  | COG
9340 |  |  | renew 07/27/21 7/15/1983 | renew 09/17/21 6/11/1984 | Wharton County Generation LLC | Newgulf | Wharton | GE F7 | 1 | 79 |  | 75 | S |  | SC
9346 | 612M2 |  | renew 03/26/21 7/25/1983 | renew pending 2/7/1984 | Air Liquide (origin. Bayou Cogen) | La Porte | Harris | GE F7EA | 4 | 80 | 320 | 5 (CT only) 7 (CT + duct) | S | 15 (CT only) 20 (CT + duct) | COG
9241A | 493M4 | S 76375 | renew 03/09/12 7/22/1983 | renew 04/08/13 10/13/1983 | Optim En. Altura (Cogen Lyondell/ARCO) | Channelview | Harris | GE F7 | 5 | 75 | 500 | 36 - 24 | S + DLN |  | CC
9044 |  | S 49187 | renew 09/24/19 3/10/1982 | renew 01/13/20 6/7/1982 | Blue Cube Operations LLC (prev. Dow Chemical) | Freeport | Brazoria | GE F7 | 3 (1 retired) | 70 |  | NC | DLN (2) | 35 | CC/COG
7647B | 276M2 |  | renew 09/29/20 5/22/1979 | renew 09/30/21 12/6/1979 | Oxy Vinyls LP (orig. Diamond Shamrock) | La Porte | Harris | GE F7 | 3 | 80 |  | 25 (unit 1 and 2) 4 (unit 3) | DLN (units 1 and 2), SCR (unit 3) | 25 | CC/COG
5409 |  |  | renew 04/28/16 6/2/1977 | renew 12/20/16 8/17/1977 | El Paso Electric | El Paso | El Paso | W 501B4 | 1 | 73 | 73 | 135 | W |  | SC
3914 |  |  | renew 10/30/13 11/21/1975 | renew 07/17/15 1/23/1976 | Blue Cube Operations LLC (prev. Dow Chemical) | Freeport | Brazoria | GE Frame 7C/E | 1 | 75 |  | NC | DLN (2) |  | CC
2094 |  |  | renew 01/29/13 2/25/1974 | renew 10/23/13 3/26/1974 | NRG Texas Power LLC (TH Wharton Station) | Houston | Harris | GE MS7001C | 6 | 85 |  | 55 | W |  | SC
CODES: Permit information - N# = Nonattainment area permit; S = Standard Permit; HAP = Haz Air Poll. Turbine Model - Pkg = Peaking. FO = Fuel Oil. (CO2) - CO2 capture
Control info - NC = No Controls, W or S = Water or Steam Injection, D or DLN = Dry Low NOx, LPM = Lean Pre-mix, SCR = Selective Catalytic Reduction, CO = CO Catalyst
(1) BACT, LAER or Std Permit limit (ppmvd @ 15% O2) (2) Retrofit for ozone SIP (MECT)
Cycle: Combined Cycle (CC); Simple Cycle (SC); Process steam cogeneration (COG); Compressed air energy storage (CAES); CO2 - closed supercritical CO2 Brayton
* <0.14 lb NOx/MWh and <132 ppmvd CO @ 15%O2 †Separate GHG Permit
End of worksheet
Formulas:
GHG Permit Issue Date = Table1[[#This Row],[Issue Date]]

## Pending Turbine Air Permits
TCEQ: Pending Air Permits for Gas Turbines with Electric Output Rated 20 MW or Greater
Version 2023.07.01
This is a list of pending natural gas-fired turbine projects under review by TCEQ that generate 20 megawatts (MW) or more greater electric output. It shows their permit numbers, turbine models, number of turbines, power output per turbine and site wide in MW, emissions controls, mode of operation (simple cycle [SC], combined cycle [CC], or cogeneration), and BACT emission concentrations for NOx and CO.
Disclaimer: Blank cells are intentionally blank because there is either no additional permit type associated with the NSR permit, or the information for that field is unavailable.
Permit No. | PSD | NA/S/HAP | Received | Issue Date | Company Name | City | County | Turbine Model | Number of CTs | MW per CT | Project MW | NOx (1) | Control Method | CO (1) | SC/CC | GHG Permit No. | GHG Permit Issue Date
171518 |  |  | 2023-01-13 | pending | Graphic Packaging International | Waco | McLennan | GE LM6PC | 1 | 129.3 | 129.3 | 2 | SCR + DLN + CO | 4 | CC
CODES: Permit information - N# = Nonattainment area permit; S = Standard Permit; HAP = Haz Air Poll. Turbine Model - Pkg = Peaking. FO = Fuel Oil. (CO2) - CO2 capture
Control info - NC = No Controls, W or S = Water or Steam Injection, D or DLN = Dry Low NOx, LPM = Lean Pre-mix, SCR = Selective Catalytic Reduction, CO = CO Catalyst
(1) BACT, LAER or Std Permit limit (ppmvd @ 15% O2) (2) Retrofit for ozone SIP (MECT)
Cycle: Combined Cycle (CC); Simple Cycle (SC); Process steam cogeneration (COG); Compressed air energy storage (CAES); CO2 - closed supercritical CO2 Brayton
* <0.14 lb NOx/MWh and <132 ppmvd CO @ 15%O2 †Separate GHG Permit
End of worksheet

## Voided Turbine Air Permits
TCEQ: Voided, Withdrawn, Expired, Consolidated, or Reiussed Air Permits for Gas Turbines with Electric Output Rated 20 MW or Greater
Version 2023.07.01
This is a list of natural gas-fired turbine projects previously but no longer authorized by TCEQ that generate 20 megawatts (MW) or more greater electric output. It shows their permit numbers, turbine models, number of turbines, power output per turbine and site wide in MW, emissions controls, mode of operation (simple cycle [SC], combined cycle [CC], or cogeneration), and BACT emission concentrations for NOx and CO.
Disclaimer: Blank cells are intentionally blank because there is either no additional permit type associated with the NSR permit, or the information for that field is unavailable.
Permit No. | PSD | NA/S/HAP | Received | Issue Date | Company Name | City | County | Turbine Model | Number of CTs | MW per CT | Project MW | NOx (1) | Control Method | CO (1) | SC/CC | GHG Permit No. | GHG Permit Issue Date
105810 | 1308 |  | 2012-09-12 | V 3/17/2021 | NRG Texas Pwr LLC (Cedar Bayou) | Baytown | Chambers | GE 7FA-05 or Siemens F(5) or M 501GAC | 2 | 255-264 | 728 | 2 | DLN+SCR+CO | 2 | CC | 102 | 2015-09-15
154682 |  | S | 2018-12-04 | V 1/25/2021 | ProEnergy Services LLC | Jacksonville | Cherokee | GE LM6000 | 8 | 50 | 400 | 4 | SCR +CO+W | 9 | SC
117857 |  |  | 2014-02-27 | V 9/4/2020 | Lake Creek 3 Pwr Co LLC (Luminant) | Riesel | McLennan | GE 7FA.05 or S GT6-5000F(5) | 2 | 225 or 230 | 460 | 9 | DLN | 9 | SC
122733 |  |  | 2014-08-14 | V 6/17/2020 | Halyard Energy Henderson LLC | LaRue | Henderson | GE F.03 or.05 or S F5ee | 2 | 193-232 | 386-464 | 9 | DLN | 9 | SC
129329 |  |  | 2014-12-22 | V 6/4/2020 | Halyard Energy Wharton LLC | El Campo | Wharton | GE F.03 or.05 or S F5ee | 2 | 193-232 | 388-464 | 9 | DLN | 9 | SC
156710 |  | S | 2019-05-01 | 2019-05-21 | Altajac Power Center LLC | Jacksonville | Cherokee | GE LM6000 | 3 | 50 | 150 | 4.4 | SCR | 26.3 | SC
106011 | 1310 |  | 2012-09-24 | V 3/15/2019 | Guadalupe Power Partners LP | Marion | Guadalupe | GE 7FA.03/.04 /.05 or S5000F | 2 | 192-227 | 383-454 | 9 | DLN | 9 | SC | 1310GHG | 2014-12-02
154928 |  |  | 2018-12-20 | WD 1/18/2019 | ProEnergy Services LLC | Houston | Harris | GE LM6000 | 4 | 50 | 300 | 4 | SCR + CO | 9 | SC
36889 |  |  | 1997-10-29 | V 4/9/2020 | Sabine Cogen (was HI Pwr Gen) | Orange | Orange | GE F6B | 2 | 40 | 110 | 9/5 | SCR+CO Cat | 15 | CC/COG
108411 | 1350 |  | 2013-02-22 | 2014-04-29 | Tenaska Brownsville Partners LLC | Brownsville | Cameron | MHI 501GAC | 1 or 2 | 275 | 400-800 | 2 | DLN+SCR+CO | 2 |  | 1350GHG | 2015-01-23
138152 | 1492 | N246 | 2015-12-16 | V 8/20/2019 N & PSD WD 7/15/2017 | AES Gen Dev LLC | Pasadena | Harris | GE 7FA | 2 | 224 | 448 | 5 | DLN | 9 | SC | 153 | Withdrawn 7/5/2017
102731 | 1294 |  | 2012-05-10 | V 8/15/2019 | NRG Texas Pwr LLC SR Bertron | La Porte | Harris | GE 7FA-05 or Siemens F(5) or M 501GAC | 2 | 255 | 823 | 2 | DLN+SCR+CO | 2 | SC/CC | 104 | 2015-09-15
110357 | 1452 | W | 2015-03-16 | PSD Withdrawn 3/4/2019 | Tradinghouse Pwr Co LLC (Luminant, switching to CC) | Waco | McLennan | GE FA.05 or S F5ee | 4 | 210 or 231 | 1,440 or 1,624 | 2 | DLN + SCR + CO | 2 | CC | 132 | Withdrawn 3/4/2019
118611 |  |  | 2014-03-28 | V 5/2/2018 | Coleto Creek Power LP (GDF Suez NA) | Fannin | Goliad | GE 7FA.05 | 1 | 230 | 230 | 9 | DLN | 9 | SC
116603 |  | S | 2014-01-10 | V 6/13/18 | TXP Winkler, LLC | Wink | Winkler | GE LM6000 | 3 | 51.3 | 154 | 4 | DLN + SCR
116605 |  | S | 2014-01-10 | V 6/13/18 | TXP Sealy, LLC | Sealy | Austin | GE LM6000 | 3 | 51.3 | 154 | 4 | DLN + SCR
116607 |  | S | 2014-01-10 | V 6/13/18 | TXP Reeves, LLC | Coyanosa | Reeves | GE LM6000 | 3 | 51.3 | 154 | 4 | DLN + SCR |  | SC
122987 |  | S | 2014-08-18 | V 6/13/18 | TXP Ricebird LLC | El Campo | Wharton | GE LM6000 | 3 | 51 | 152 | 4 | DLN + SCR | 8 | SC
114911 | 1380 |  | 2013-11-12 | V 11/7/2017 | Lon C. Hill LP | Corpus Christi | Nueces | GE 7FA.05, 7FA.04, or S SCC6-5000F, SST6-5000 | 2 | 195-240 | 625-740 | 2 | DLN+SCR+CO | 2 | CC | 1380GHG | 2014-10-28
114698 | 1378 |  | 2013-10-25 | V 7/18/2017 | Tenaska Roans Prairie Partners, LLC | Shiro | Grimes | GE 7FA.05, 7FA.04, or S GT6-5000F(5) | 3 | 169 - 231 | 507 - 694 | 9 | DLN | 9 | SC | 1378GHG | 2014-08-01
122401 | 1428 |  | 2014-08-04 | V 1/9/2018 | Apex Tx Pwr LLC - Neches Station | Cuney | Cherokee | F Class | 4 SC or 2 CC | No data | 930 SC 794 CC | 9 SC or 2 CC | DLN SC DLN + SCR + CO CC | 9 SC or 4 CC | SC/CC | 111 | 2016-03-24
135021 | 1468 |  | 2015-08-12 | V 5/9/2017 | Panda Sherman Power LLC | Sherman | Grayson | GE H.02 MHI 501JAC,or S SCC6-8000H | 1 | 287 - 330 | 470 - 540 | 2 | DLN + SCR + CO | 2 | CC | 144 | Void
9292A | 605M2 |  | 1983-03-04 | V 4/27/2017 | Calpine - Clear Lake Cogen. Ltd. | Pasadena | Harris | W 501D | 3 | 100 | 400 | 75 | W |  | CC
35335 | 880M1 |  | 2015-08-27 | WD 3/31/2017 | Occidental Chemical (Ingleside): Amend project withdrawn 3/31/2017 | Gregory | San Patricio | GE FA.04 or S SGT6-5000F4 | 1 | 185 | 260 | 2 | DLN + SCR | 4 | CC/COG | 142 | Withdrawn 3/31/2017
107055 |  | S | 2012-11-26 | 2013-02-06 | Apex Matagorda En Ctr | Clemville | Matagorda | D-R EA-418 (CAES) | 2 | 158 | 317 | 2.5 | W+SCR+CO | 5 | CAES | 107055 | 2014-04-14
22043 | 818 |  | 1992-11-09 | V 7/22/2016 | Equistar Chemical (Quantum) | Deer Park | Harris | GE F6 | 2 | 36 | 96 | 15 | D | 25 | CC/COG
99181 |  |  | 2011-10-25 | V 4/25/2016 | NRG Tx Pwr LLC - WA Parish Gen Sta | Thompson | Fort Bend | GE F7EA | 1 | 80 | 80 | 5 | DLN | 25 | SC
71739 | 1043 |  | 2004-04-02 | V 9/23/2015 | Cobisa-Greenville LLP (EXP) | Greenville | Hunt | GE F7FA or W 501F/G | 6 or 4 | 170 - 230 | 1800 | 2 | SCR | 25 | CC
96336 | 1256 |  | 2011-05-27 | V 8/28/2015 | Calhoun Port Authority - ES Joslin | Point Comfort | Calhoun | GE F7FA | 3 | 185 | 887 | 2 | DLN+SCR | 9 | CC
102294 | 1290 |  | 2012-04-20 | V 2/5/2015 | El Paso Electric (Reissued as S No. 123471) | El Paso | El Paso | GE LMS100 | 4 | 100 | 400 | 2.5 | W+SCR+CO | 4 | SC | 1290GHG | 2014-03-15
25034 |  |  | 1994-05-16 | V 12/19/2014 | Union Carbide | Texas City | Galveston | GE F6 | 1 | 38 | 38 | 15 | D | 25 | COG
3941 |  |  | 1975-12-10 | V 6/30/2014 | Dow Chemical | Freeport | Brazoria | W501A | 2 | 45 |  | NC |  |  | COG
16840 | 688 |  | 1985-11-22 | V 2/7/2012 | Fina Oil | Port Arthur | Jefferson | GE F6 | 2 | 37 |  | 50 | S/W |  | COG
9244 |  |  | 1982-12-14 | V 11/16/2011 | Motiva Enterprises (Texaco) | Port Arthur | Jefferson | GE F6 | 1 | 37 |  | NC |  |  | COG
9344 | 243M2 |  | 1983-07-20 | V 9/14/2011 | Coastal Refining & Marketing | Corpus Christi | Nueces | GE F5 | 2 | 25 |  | 112 | D |  | COG
99691 |  |  | 2011-11-21 | V 12/2/2015 | Golden Spread El. Coop Mustang Unit 6 (Cons into 72579, 11/30/2015) | Denver City | Yoakum | GE F7FA | 1 | 168 | 168 | 9 | DLN | 8 | SC
9047 |  |  | 1982-03-10 | V 8/18/2010 | Dow Chemical | Freeport | Brazoria | W 501D | 1 (retired) | 100 |  | NC |  |  | CC/COG
9046 |  |  | 1982-03-10 | V 8/16/2010 | Dow Chemical | Freeport | Brazoria | W 501D | 2 (retired) | 100 |  | NC |  |  | CC/COG
84289 | 1125 | N75 | 2008-03-07 | V 9/16/2020 | Pondera Dev LLC - King Pwr Station (EXP) | Houston | Harris | GE 7FA.07 or HA.01 | 2 | 230 | 900 | 2 | DLN+SCR+CO | 2 | CC
9045 |  |  | 1982-03-10 | V 3/4/2010 | Dow Chemical | Freeport | Brazoria | W 501D | 2 (retired) | 100 |  | NC |  |  | CC/COG
82426 | 1100 | N69 | 2007-07-19 | V 2/9/2016 | Exelon/EXTEX LaPorte Ltd P (EXP) | Dallas | Dallas | S GT6-5000F | 2 | 194 | 395 | 2.5 | DLN+SCR+CO | 8 | SC | EPA-issued? | not at TCEQ
87222 | 1200 | HAP53 | 2008-12-29 | WD 12/12/2014 | MyPower Corp - Lakeside En Ctr (WD) | Fairfield | Freestone | S GT6-5000F | 2 | 193.5 | 640 | 2 | DLN+SCR | 9
104511 |  | S | 2012-07-18 | 2012-09-01 | Apex Bethel En Ctr LLC (EXP) reiss. 118876 | Tenn. Colony | Anderson | D-R EA-418 (CAES) | 2 | 158 | 317 | 2.5 | W+SCR+CO | 5
17369 | 713 |  | 1986-05-29 | V 7/14/2009 | Exxon | Baytown | Harris | W 251B8 | 2 | 43 |  | 75 | S |  | COG
9517 | 642 |  | 1984-08-28 | V 7/1/2009 | Ineos USA (orig. Amoco) V 2/09 reiss 95 | Alvin | Brazoria | GE F6 | 1 | 37 |  | 75 | S |  | COG
83207 | 1106 |  | 2007-10-25 | V 12/2/2016 | Lamar Power Partners II LLC (EXP) | Paris | Lamar | GE F7FA or M 501G | 2 | 170 or 200 | 620 or 910 | 2 | DLN+SCR | 15
110577 |  | S | 2013-06-04 | V 1/15/2014 | Frame Switch En Inc (proj chg to RICE) | Hutto | Williamson | P&W FT4000 | 2 | 60 | 120 | 3.5 | SCR+CO | 12.3
109147 | 1356 |  | 2013-04-01 | WD 9/18/2013 | Golden Spread El. Coop. - Floydada Sta. | Floydada | Floyd | GE 7FA.05 | 1 | 190 | 190 | 9 | DLN | 9
100129 | 1284 | N152 | 2011-12-20 | WD 8/3/2012 | Freeport LNG Development, L.P. (WD) | Freeport | Brazoria | GE 7EA | 1 | 90 | 90 | 2 | DLN+SCR+CO | 4
17740 | 716 | No data | 1986-11-17 | V 5/29/2012 | Luminant (Encogen One)(decomm) | Sweetwater | Nolan | GE F7E (2), F6 | 3 | 80,37 | No data | 42 | S
86013 | 1163 | N94 HAP33 | 2008-09-02 | V 8/31/2009 | NRG S.R. Bertron IGCC (CO2) | La Porte | Harris | Gasification Units | 2 | No data | 550
85862 | 1153 |  | 2008-08-13 | V 4/15/2009 | Grimes County En Ctr, LLC | Singleton | Grimes | GE 7FA | 4 | 170 | 1160 | 2 | DLN+SCR | 12
85534 | 1143 |  | 2008-06-27 | WD 10/11/2012 | Navarro Generating LLC (WD) | Richland | Navarro | F Class | 2 | 232 | 780 | 2 | DLN+SCR+CO | 5
84248 | 1128 | N79 | 2008-02-28 | WD 2/9/2009 | NRG Power - SR Bertron | La Porte | Harris | F Class | 4 | 200 | 1300 | 3 | DLN+SCR+CO | 5
20862 | 799 |  | 1991-05-20 | V 12/15/2009 | Exxon Mobil Oil - refinery cogen | Beaumont | Jefferson | GE F6 | 1 | 37 | 37 | 9 | S+SCR | 10 | COG
83784 | 1116 | N73 | 2008-01-04 | V 10/6/2015 | Entergy Lewis Creek Plant (EXP) | Willis | Montgomery | GE F7FA | 2 | 167 | 500 | 2 | DLN+SCR | 12
83690 | 1113 |  | 2007-12-21 | WD 1/6/2010 | Pin Oak Creek Energy LLC | Richland | Navarro | F Class | 4 | 200 | 1400 | 2 | DLN + SCR | 2
83642 | 1115 |  | 2007-12-13 | V 9/20/2019 | Pattillo Branch Pwr (LS Pwr) (EXP) | Savoy | Fannin | F Class | 4 | 200 | 1400 | 2 | DLN+SCR+CO | 2
20250 |  |  | 1990-07-24 | V 3/25/2009 | Praxair | Texas City | Galveston | GE F6 | 1 | 37 | 37 | 25 | S | 46 | COG
32263 | 866 |  | 1996-04-01 | V 2/16/2009 | Calpine - Pasadena Cogen LLC | Pasadena | Harris | W 501F | 1 | 180 | 240 | 12 | S,SCR | 20 | CC/COG
83390 | 1108 |  | 2007-11-16 | V 10/9/2019 | NRG - Cedar Bayou (Unit 5) (EXP) | Eldon | Chambers | F, G, or 7FB | 2 | 200 | 700 | 2 | DLN+SCR | 18
83378 | 1105 |  | 2007-10-31 | V 10/14/2019 | Madison Bell Partners LP (EXP) | Madisonville | Madison | GE F7E | 4 | 75 | 550 | 2 | DLN+SCR | 17.5
82244 | 1098 |  | 2007-06-21 | V 5/11/2018 | NavasotaWhartonCol Bend Unit 3(EXP) | Wharton | Wharton | GE F7EA | 2 | 75 | 225 | 2 | DLN+SCR | 27
82303 | 1099 |  | 2007-06-21 | V 2/19/2019 | Navasota Odessa Unit 3 (EXP) | Odessa | Ector | GE F7EA | 2 | 75 | 225 | 2 | DLN+SCR | 27
81853 | 1092 |  | 2007-05-04 | WD 8/31/2009 | Occidental Energy Ventures Corp | Denver City | Yoakum | ???? | 3 | ??? | 700 | 2 | DLN + SCR | 15
95 | 854M2 |  | 2007-01-03 | WD | Ineos USA LLC (deleted from flex P proj) | Alvin | Brazoria | Solar 130S | 2 | 15 | 30 | 5 | SCR | 32
45642 | 979M1 | N036M1 | 2006-11-10 | 2007-12-21 | Calpine Deer Park - Units 5, 6 (EXP) | Deer Park | Harris | SW 501F | 2 | 180 | 530 | 2.5 | SCR | 24
80546 | No data | S | 2006-12-11 | V 6/30/2015 | NRG S.R. Bertron(peakers) (EXP) | La Porte | Harris | GE LM6000 | 4 | 50 | 200 | 5 | W + SCR | 25
80289 | 1082 | No data | 2006-10-31 | 2007-07-26 | NRG - Cedar Bayou (peakers) (EXP) | Eldon | Chambers | GE LM6000 | 8 | 50 | 400 | 5 | W + SCR | 25
79335 | No data | No data | 2006-06-30 | V 12/22/2010 | Wise County Pwr Co LP (EXP) | Poolville | Wise | GE F7EA | 4 | 81 | 324 | 9 | DLN | 25
79133 | No data | S | 2006-06-06 | V 8/27/2007 | GoldenSpread Unit 5 (V) Cons in 72579 | Denver City | Yoakum | GE 7FA (PKg) | 1 | 168 | 168 | 9 | DLN | 9
77679 | 1061 |  | 2005-12-22 | 2007-03-01 | Nacogdoches Pwr (deleted from proj) | Sacul | Nacogdoches | SW 501F | 1 | 190 | 330 | 5 | DLN+SCR | 21
9910 | 731 |  | 1994-12-30 | V 12/9/2005 | Exxon Chemicals GT/HRSG 4 | Baytown | Harris | Siem. V82.2 GE F6 | 1 3 | 100 37 | 100 111 | 9 42 | D S | 15 -- | COG
9492B | 639 |  | 1984-06-20 | V 5/30/2005 | Occidental Chemical (V - 2005) | Deer Park | Harris | GE F7 | 1 (retired) | 80 |  | 75 | S |  | COG
445 |  |  | 1972-11-01 | V 5/12/2004 | HL&P TH Wharton (now #21592) | Houston | Harris | GE F7B | 2 | 57 | STAG 300 | 55 | W |  | CC
45642 | 979M1 | N036M1 | 2004-03-30 | WD 10/13/2004 | Calpine Deer Park En (add 2 units) | Deer Park | Harris | W 501F | 2 | 180 | 360 | 2.5 | SCR | 24
20065 | 780 |  | 1990-04-11 | V 9/16/2003 | Huntsman (P#20065 consol to P#16909) | Port Neches | Jefferson | GE F6 | 2 | 37 | 74 | 25 | LPM | 25 | COG
55629 | No data | S | 2003-06-26 | V 9/8/2003 | Brownsville PUB (V) | Brownsville | Cameron | GE LM6000 | 1 | 50 | 50 | 5 | SCR | 32
54114 | 1031 | N055 | 2003-01-09 | V 11/14/2007 | Bayport Energy Center LP (EXP) | Pasadena | Harris | GE F6B | 2 | 40 | 80 | 3.5 | SCR | 17.2
17625 | 704 |  | 1986-09-17 | V 6/11/2003 | Koch Refining Co. | Corpus Christi | Nueces | GE F6 | 1 | 37 |  | 42 | S |  | COG
49293 | 1015 |  | 2001-09-21 | V 1/13/2006 | Steag - Sterne Elec Gen Fac (EXP) | Sacul | Nacogdoches | SW 501F | 3 | 190 | 1000 | 5 | SCR | 21
48500 | 1013 |  | 2001-07-16 | WD 11/20/2001 | STEAG Power LLC (WD) | Ennis | Ellis | W 501G | 4 | 200 | 1400 | 5 | SCR | 35
46603 | No data |  | 2001-04-26 | V 8/4/2004 | Ridge En Storage & Grid Servs (EXP) | Clemville | Matagorda | DR T6-EA418 | 4 | 134 | 538 | 9 | SCR | 25
47318 | 1009 |  | 2001-03-07 | V 11/9/2005 | Hartburg Power LP (EXP) | Deweyville | Newton | GE F7FA | 3 | 277 | 800 | 5 | SCR | 15
46665 | 1003 |  | 2000-12-14 | V 5/19/2004 | Ennis Tractebel II LP (V 05/19/04) | Ennis | Ellis | W 501G | 2 | 230 | 815 | 5 | SCR | 9
46536 | No data |  | 2000-11-22 | WD 10/4/2001 | Texas Bayou En Ctr (WD-PBR) | Texas City | Galveston | GE LM2500 | 1 | 25 | 25 | 4.2 | SCR | 25
46532 | No data |  | 2000-11-21 | V 12/23/2003 | Celanese, Ltd (Turbines Deleted) | Pasadena | Harris | GE LM6000 | 6 | 47 | 284 | 5 | SCR + CO | 5
46470 | 990 |  | 2000-11-17 | V 11/20/2001 | STEAG Power LLC (AV & V) | Ferris | Ellis | GE F7FA | 4 | 175 | 1200 | 3.5 | SCR | 20
46192 | 983 |  | 2000-10-24 | V 5/23/2012 | Innovene (was BP, Amoco) (EXP) | Alvin | Brazoria | GE F6B | 2 | 35 | 70 | 3.5 | SCR | 25 | COG
42179 | 955 | N021 | 2000-11-16 | WD 11/7/2002 | Channel Energy (Add 4th Cogen) (V) | Pasadena | Harris | W 501F | 1 | 180 | 180 | 3.5 | SCR | 25
46426 | 999 |  | 2000-11-13 | 2003-10-08 | Texas Petrochemicals, LP (not built) | Houston | Harris | GE F7EA | 2 | 81 | 581 | 5 | SCR | 25
43965 | 966 | N026 | 2000-11-06 | 2002-12-31 | Steag/Brazos V. add 2 CCTs (EXP) | Thompsons | Fort Bend | GE F7FA | 2 | 170 | 660 | 3.5 | SCR | 25
9378 | 619 |  | 1983-10-12 | V 8/30/2002 | Amoco Chemicals | Texas City | Galveston | GE F6 | 1 | 37 |  | 75 | S |  | COG
45843 | 982 | N037 | 2000-10-02 | V 7/25/2011 | Calpine Amelia En Ctr (EXP) | Amelia | Jefferson | W 501F | 3 | 180 | 1030 | 3.5 | SCR | 22
44174 | 968 | N028 | 2000-04-13 | V 7/9/2007 | MC Energy Partners, LP (V) | Montgomery | Montgomery | GE F7FA | 2 | 170 | 660 | 3 | SCR | 25
44175 | 969 | N029 | 2000-04-13 | V 9/7/2006 | Cedar Power Partners, LP(EXP) | Dayton | Liberty | GE F7FA | 2 | 175 | 800 | 3 | SCR | 25
43178 | 962 |  | 1999-12-30 | V 5/19/2008 | Westvaco Texas LP (Expired) | Evadale | Jasper | GE LM6000PC | 2 | 42 | 84 | 5 | SCR + CO | 22
42905 | 961 | N023 | 1999-11-24 | WD 3/14/2002 | Texas Industrial Power (WD) | Mt. Belvieu | Chambers | W 501FD | 1 | 177 | 193 | 5 | SCR | 25
42774 | 960 |  | 1999-11-10 | V 10/8/2003 | West Texas Energy Ltd Part (EXP) | El Paso | El Paso | ABB-GT24 | 2 | 180 | 500 | 3.5 | SCR | 5
42169 | 954 |  | 1999-08-25 | V 4/29/2003 | Duke Energy Jack, LP (EXP) | Jacksboro | Jack | GE F7FA | 2 | 170 | 620 | 5 | SCR | 20
42086 | 952 |  | 1999-08-16 | V 12/1/2003 | Palestine Generation LLC (EXP) | Palestine | Anderson | GE F7FA | 6 | 170 | 1600 | 5 | SCR | 15
41802 | 947 | N019 | 1999-07-12 | V 4/2/2003 | Chambers Energy Facility (V) | Houston | Harris | ABB GT24 OTC | 8 | 180 | 2200 | 3.5 | D + SCR + CO | 20
41774 | 945 |  | 1999-07-06 | V 4/29/2003 | Gateway Power Project, LP (EXP) | Gilman | Upshur | GE F7FA | 3 | 170 | 800 | 5 | SCR | 7.4
41606 | 944 |  | 1999-06-14 | V 5/22/2003 | Duke Energy Bell LP (EXP) | Temple | Bell | GE F7FA | 2 | 170 | 520 | 5 | SCR | 20
41472 | 942 |  | 1999-05-27 | V 5/6/2010 | Kaufman Cogen, LP (EXP) | Mesquite | Kaufman | GE F7FA | 2 | 170 | 620 | 5 | SCR | 20
41013 | 937 |  | 1999-04-05 | V 5/22/2003 | Archer Power Partners LP (EXP) | Lakeside City | Archer | GE F7FA | 4 | 170 | 1000 | 5 | SCR | 9
9241A | 493M4 |  | 1999-03-04 | 1999-11-05 | Cogen Lyondell (Turbine #7) (EXP) | Channelview | Harris | W 501F (Pkng) | 1 | 160 | 160 | 25 | D | 25
40699 | 932 |  | 1999-02-23 | V 3/17/2003 | ExxonMobil (Cons into 19566) | Beaumont | Jefferson | GE F7FA | 3 | 170 | 740 | 5 | SCR | 10/25
40619 | 933 |  | 1999-02-11 | V 5/23/2012 | Mirant Parker LLC (SEI) (EXP) | Weatherford | Parker | GE F7FA/F7EA | 2/2 | 170/82 | 650 | 9/9 | D | 9/25
38484 | 911 | N013 | 1998-05-29 | WD 9/22/2000 | Air Products, Inc (V ) | La Porte | Harris | W 501F | 1 | 168 | 240 | 9/5 | SCR | 20
37302 | 895 |  | 1997-12-29 | V 6/23/2003 | Edinburg Energy (EXP) | Edinburg | Hidalgo | ABB GT-24 | 4 | 180 | 815 | 15 | D | 10
37227 | 894 | N005 | 1997-12-12 | V 7/18/2003 | Air Liquide America Corp (V ) | La Porte | Harris | GE F7EA | 3 | 81 | 243 | 9/5 | SCR | 25
34824 | 877 |  | 1997-05-09 | V 12/1/2008 | Gregory Pwr (V)(failed to renew) | Gregory | San Patricio | GE F7FA | 2 | 168 | 336 | 15 | D | 20
33166 | 870 |  | 1996-07-22 | V 6/30/2003 | Longview Generating, LP (EXP) | Longview | Gregg | GE F7FA | 1 | 180 | 180 | 9 | D | 8
23962 | 837 |  | 1993-12-03 | V 2/6/1998 | West Campus Cogeneration (EXP) | College Stn. | Brazos | GE F6 | 2 | 37 | 75 | 9-14 | D
19566 | 932 |  | 1999-02-23 | V 3/30/2009 | ExxonMobil (originally 40699) (Cons into 49138, 11/24/09) | Beaumont | Jefferson | GE F7FA | 3 | 170 | 740 | 5 | SCR | 10/25 | CC/COG
9910 | 731M2 |  | 2002-10-04 | V 12/9/2005 | ExxonMobil Corp - Baytown (Cons into 3452, 8/24/05) | Baytown | Harris | GE F7FA | 1 | 170 | 170 | 3 | SCR | 7.4 | COG
CODES: V = Void, AV = Admin Void, EXP = Expired, WD = Withdrawn, DEL = Deleted, Cons = Consolidated, S = Standard Permit, PBR = Permit by Rule
(1) BACT (ppmvd @ 15% O2)
CODES: Permit information - N# = Nonattainment area permit; S = Standard Permit; HAP = Haz Air Poll. Turbine Model - Pkg = Peaking. FO = Fuel Oil. (CO2) - CO2 capture
Control info - NC = No Controls, W or S = Water or Steam Injection, D or DLN = Dry Low NOx, LPM = Lean Pre-mix, SCR = Selective Catalytic Reduction, CO = CO Catalyst
(1) BACT, LAER or Std Permit limit (ppmvd @ 15% O2) (2) Retrofit for ozone SIP (MECT)
Cycle: Combined Cycle (CC); Simple Cycle (SC); Process steam cogeneration (COG); Compressed air energy storage (CAES); CO2 - closed supercritical CO2 Brayton
End of worksheet
* <0.14 lb NOx/MWh and <132 ppmvd CO @ 15%O2 †Separate GHG Permit
End of worksheet